## Sheet1
Common AEI Field Process | Basic | Basic and Typical
Type of Contaminant | Process Examples | Design Velocity (FPM Branch/Main)
Welding Smoke | MIG welding, stick, tig, arc, & flux core | 2,800/3,000FPM Typical
Oil Mist/Smoke | CNC machining, screw machines, cold headers | 2,800/3,000FPM Typical
Grinding Dust/Sanding Dust | Surface grinders, abrasive blast, & grinders | 4,000/4,500FPM Typical
Woodworking Dust | Lathes, Planers, Shapers, Jointers, misc wood | 4,000/4,5000FPM Typical
Note:
Due to relatively high pressure drop and resulting
flow restrictions, velocities in excess of 3,500FPM
should normally be avoided. Large particulate
should be allows to fall out at the hood or inside
the machine; leaving the air cleaner or collector
to collect the fine respirable fines.
Always refer to the Industrial Ventilation Guide for
recommended practices on lateral drops (branch
transitions), corresponding bends, and elbows.
Fan inlet restrictions can create system effects
that will ultimately reduce fan performance.
System Pressure Drop - Examples (Fan Selections)*
Weld Fume Collector System 10-12"SP
Mist Collection System 2-4"SP
Woodworking Dust Collection System 12-14"SP
Exhaust System w/Swing Arms 10-12"SP (w/o Collector)
Exhaust System w/Welding Booths 8"SP (w/o Collector)
*Note: I can teach you the equivalent foot method for
figuring the static pressure of a system from the hood
to the fan outlet and with all the related system accessories.
The system is figured on the last leg, worst leg configuration, and
back. The higher the velocity the higher the resistance & HP.