Centurion Tools

Rework &

Test Report

May 2, 2012

- As Found Data – reading taken with old second stage filters

  - As Found Flow Data

    - Machine #1 – 664 CMF

    - Machine #2 – 548 CFM

    - Machine #3 – 716 CFM

    - Machine #4 – 600 CFM

    - Absolent Inlet – 2649 CFM

  - Dust Trac Reading

    - Machine outlet – 0.155 to 0.160 mg/m3

    - Absolent Inlet – 0.160 mg/ m3

    - Absolent Outlet – 0.025 mg/ m3

    - General Area - 0.035 mg/ m3

- Rework Perform

  - Installed new external gauges

    - 1st Stage – 0-500pa green area

    - 2nd Stage – 0-500pa green area

    - HEPA – 0-600pa green area

  - Old Gauges

    - 1st Stage – 0-500pa green area

    - 2nd Stage – 0-600pa green area

    - HEPA – 0-600pa green area

  - Gauge Reading (with new 2nd stage filters (S3B3/595)

    - New – gauges reading where steady and repeatable.

      - 1st Stage – 300pa

      - 2nd Stage – 500pa

      - HEPA – 300pa

    - Old

      - 1st Stage – 0 - 400pa unit running or off

      - 2nd Stage – 400pa (fairly steady)

      - HEPA – 300pa (fairly steady)

  - Installed two new 2nd stage filters (S3B3/595) and removed all spacer clips.  Filters tightened correctly without spacer clips.

  - Removed 1st HEPA filter

    - Inspected motor compartment and found it clean and free of oil.

    - Checked gauge lines and could not see any oil.

    - 1st stage gauge showed a reading with gauge lines removed, but returned to zero after the unit was cycled.

    - One filter locking cam bar broke upon loosening of the filters.  It was replaced with one repaired previously by Centurion Tool.  All spacer clips where removed.

  - Door Gasket Replacement

    - Removed all three filter compartment gaskets

    - Installed new gasket material to door.

    - Readjusted door latches.

- As Left Flow Data – reading taken with new second stage filters

  - As Left Flow Data

    - Machine #1 – 600 CMF

    - Machine #2 – 600 CFM

    - Machine #3 – 605 CFM

    - Machine #4 – 600 CFM

    - Absolent Inlet – 2403 CFM

No Dust Trac data with new filters due to machines being shut down.

Bill Boisvert

Bill Boisvert, Project Manager

Avani Environmental Intl., Inc.

Cell: 919-971-3910

Office: 919-570-2862 x219

E-mail: bboisvert@avanienvironmental.com