Customer: 	Eaton Corp.

2564 Durham Road

Roxboro, NC 27573

Contact:	 Mike Riley

Phone: 	 	336-503-6631

Email:

Date:  5/10/12

Project #:

Sales Order #:

Serial #: 20030167

Model #: ODR-9000

AEI Crew:  Bill B. & Mark P.

SCOPE OF PROJECT:        Installation – (Service) – Warranty – Demo – Delivery - Engineering

- Installed blast gates with screen caps on two 10” lines

  - Adjusted gates to 1/2 open.

- Completed air flow balance.

  - See tables below:

| Machine 5 |  | Machine 3 |  | Machine1 |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | ODR-9000 |
| Machine 6 |  | Machine 4 |  | Machine 2 |  |  |

|  |  | Location # | Absolent Inlet |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Test Point | VP | V | CFM |  |  |  |
|  |  | 1 | 0.59 | 3076 | 6708 |  |  |  |
|  |  | 2 | 0.72 | 3398 | 7410 |  |  |  |
|  |  | 3 | 0.77 | 3514 | 7663 |  |  |  |
|  |  | 4 | 0.75 | 3468 | 7563 |  |  |  |
|  |  | 5 | 0.81 | 3605 | 7860 |  |  |  |
|  |  | 6 | 0.66 | 3254 | 7095 |  |  |  |
|  |  | 7 |  | 0 | 0 |  |  |  |
|  |  | 8 |  | 0 | 0 |  |  |  |
|  |  | Average | 0.72 | 3390 | 7393 |  |  |  |
|  |  | Duct Area: | 2.18 |  |  |  |  |  |
|  |  | Length | Width | Area SF |  |  |  |  |
|  |  |  |  | 0.00 |  |  |  |  |
|  |  |  | Diameter |  |  |  |  |  |
|  |  |  | 20 | 2.18 |  |  |  |  |
| Location # | Machine 1 |  |  |  | Location # | Machine 2 |  |  |
| Test Point | VP | V | CFM |  | Test Point | VP | V | CFM |
| 1 | 0.76 | 3491 | 685 |  | 1 | 0.78 | 3537 | 694 |
| 2 | 0.68 | 3303 | 648 |  | 2 | 0.75 | 3468 | 681 |
| 3 | 0.77 | 3514 | 690 |  | 3 | 0.68 | 3303 | 648 |
| 4 |  | 0 | 0 |  | 4 |  | 0 | 0 |
| 5 |  | 0 | 0 |  | 5 |  | 0 | 0 |
| Average | 0.74 | 3437 | 675 |  | Average | 0.74 | 3437 | 675 |
| Duct Area: | 0.20 |  |  |  | Duct Area: | 0.20 |  |  |
| Length | Width | Area SF |  |  | Length | Width | Area SF |  |
|  |  | 0.00 |  |  |  |  | 0.00 |  |
|  | Diameter |  |  |  |  | Diameter |  |  |
|  | 6 | 0.20 |  |  |  | 6 | 0.20 |  |
| Location # | Machine 3 |  |  |  | Location # | Machine 4 |  |  |
| Test Point | VP | V | CFM |  | Test Point | VP | V | CFM |
| 1 | 1.25 | 4478 | 879 |  | 1 | 1.10 | 4200 | 824 |
| 2 | 1.02 | 4045 | 794 |  | 2 | 1.06 | 4123 | 809 |
| 3 | 1.01 | 4025 | 790 |  | 3 | 1.04 | 4084 | 802 |
| 4 |  | 0 | 0 |  | 4 |  | 0 | 0 |
| 5 |  | 0 | 0 |  | 5 |  | 0 | 0 |
| Average | 1.09 | 4188 | 822 |  | Average | 1.07 | 4136 | 812 |
| Duct Area: | 0.20 |  |  |  | Duct Area: | 0.20 |  |  |
| Length | Width | Area SF |  |  | Length | Width | Area SF |  |
|  |  | 0.00 |  |  |  |  | 0.00 |  |
|  | Diameter |  |  |  |  | Diameter |  |  |
|  | 6 | 0.20 |  |  |  | 6 | 0.20 |  |
| Location # | Machine 5 |  |  |  | Location # | Machine 6 |  |  |
| Test Point | VP | V | CFM |  | Test Point | VP | V | CFM |
| 1 | 0.62 | 3154 | 619 |  | 1 | 0.67 | 3278 | 643 |
| 2 | 0.60 | 3102 | 609 |  | 2 | 0.60 | 3102 | 609 |
| 3 | 0.58 | 3050 | 599 |  | 3 | 0.65 | 3229 | 634 |
| 4 |  | 0 | 0 |  | 4 |  | 0 | 0 |
| 5 |  | 0 | 0 |  | 5 |  | 0 | 0 |
| Average | 0.60 | 3102 | 609 |  | Average | 0.64 | 3204 | 629 |
| Duct Area: | 0.20 |  |  |  | Duct Area: | 0.20 |  |  |
| Length | Width | Area SF |  |  | Length | Width | Area SF |  |
|  |  | 0.00 |  |  |  |  | 0.00 |  |
|  | Diameter |  |  |  |  | Diameter |  |  |
|  | 6 | 0.20 |  |  |  | 6 | 0.20 |  |

- Sealed all test hopes with aluminum tape.

Please feel free to call with any concerns.

Review, comment as needed, sign and e-mail (or fax) signed page only back to myself or Bob Venezia.

Thanks,

Bill Boisvert

Bill Boisvert - Cell (919) 971-3910

Project Manager – Avani Environmental

E-mail bboisvert@avanienvironmental.com

CUST0MER REMARKS: _____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________