- AMTECH AT DUST COLLECTOR ORDER SPECS      SALES CONTACTS:

- Ken Haga

- Bob Venezia

- [ONE SPEC SHEET PER IDENTICAL UNIT(S)]

FOR OFFICE USE ONLY:  Order Number: 	Engineering Req.   YES   NO          REV.____________

DATE: March 4th, 2008

SOLD TO: Wesco Welding Supply (LA Branch)	SHIP TO:   Mississippi Gulf Coast Community College

601 Bark Street			21500 B Street

Harvey, LA 70058			Long Beach, MS 39560

REP/DIST NAME: Industrial Air Quality, Inc.	REQUESTED SHIP DATE:  March 27th, 2008

UNIT DESCRIPTION: Model AT-12 w/Side Inlet & Discharge	QUANTITY:  (1) 	TAG #: WELD SHOP

- OUTLINE DRAWINGS

FOR APPROVAL (Drawings are for approval, production will not be scheduled until signed & approved drawings are received by AMTECH)

- APPLICATION INFORMATION

- APPLICATION DESCRIPTION: Vocational Welding Shop	DUST TYPE: Medium to Fine

AIR VOLUME: 11,278CFM     EXTERNAL STATIC: 4.0”     INTERNAL STATIC: (4” TO 6”) 8.0”     TOTAL STATIC: 12.0”

AIR-TO-MEDIA RATIO: 1.85:1	UNIT INSTALLATION LOCATION:      INSIDE      OUTSIDE

- FILTER INFORMATION

80/20 POLYESTER BLEND (STD.)      80/20 POLYESTER BLEND FR    100% CELLULOSE    SPUNBOND     100% HO SPUNBOND         80/20 POLYESTER BLEND WIDE PLEAT     80/20 POLYESTER BLEND FR WIDE PLEAT     OTHER, Describe                FILTER AREA 6,096 (FT2 MEDIA)

- AIR INLET SIZE

TOP INLET(S) –DIAMETER OF FLANGE:

SIDE INLET(S)- DIAMETER OF FLANGE: 28”D    (Recommended for Plasma, Laser & Welding)

ABRASIVE INLET(S)             SPECIAL INLET- Describe

- PULSE CONTROL INFORMATION

TIMER BOARD WITH MAGNEHELIC GAGE NEMA 12 (STD.)      PC TURBO ON DEMAND DIGITAL REVERSE PULSE CONTROL NEMA 4

STANDARD TOP MOUNT BLOWER    TOP DISCHARGE	SIDE DISCHARGE

3HP 15”FAN    5HP 15”FAN    5HP 16”FAN    7.5HP 16”FAN   10HP 18”FAN    15HP 18”FAN    20HP 20”FAN

25HP 20”FAN  30HP 22”FAN  40HP 22”FAN  OTHER, Describe: 22”ILC w/40HP

BLOWER OPTIONS:                ALUMINUM FAN WHEEL                   EXPLOSION PROOF MOTOR

CUSTOM TOP MOUNT BLOWER, Describe

GROUND MOUNT BLOWER

BLOWER SUPPLIED BY CUSTOMER/CONTRACTOR             AMTECH GROUND MOUNT BLOWER, Describe

ROTATION:     CLOCKWISE(Std)      COUNTERCLOCKWISE 	MOTOR LOCATION (Viewed from drive side):   Right     Left

DISCHARGE DIRECTION:    UPBLAST     TOP HORIZONTAL   OTHER, Describe

- MOTOR STARTER

NO	     YES            AT-MS (DISCONNECTS NOT SUPPLIED)	  NEMA1 COMBINATION DISCONNECT

SYSTEM VOLTAGE

230/3/60                     460/3/60

Special     115/1/60            230/1/60              208/3/60            575/3/60                 Other, Describe

ORDER NUMBER _________________

- SILENCER INFORMATION

NONE      STANDARD UPBLAST SILENCER     STANDARD SIDE DISCHARGE SILENCER     SPECIAL SILENCER, Describe

Supplied by IAQ (Future)

- HINGED EXPLOSION VENT WITH BRIXON LATCHES

NO    YES          YES - SPECIAL, Describe       KSt VALUE

- HOPPER ARRANGEMENT

STANDARD   DUST DRAWER

SCREW CONVEYOR - DISCHARGE RIGHT     SCREW CONVEYOR - DISCHARGE LEFT

SPECIAL, Describe

LEG ARRANGEMENT

STANDARD

SHORTEN LEGS   55GAL.-5”         30GAL.-11”         20GAL.-17”               INCREASE LEGS UP TO 12”

SPECIAL, Hopper Discharge to ground  Describe

ROTARY AIR LOCK:       YES      NO	QUANTITY:

STANDARD            8"    10"    12"    14"	    SEAL STRIPS   NONE   POLYURETHANE

CUSTOM ROTARY AIR LOCK, Describe               (Provide bolt pattern)

CLEARANCE RAL DISCHARGE TO GROUND,      IN.   (w/ std. leg height, clearance is 20 - 29" depending upon air lock selected)

- RETURN AIR FILTERS

SAFETY FILTERS:     YES - QUANTITY      	  NO    MAGNEHELIC GAGE KIT

HEPA FILTERS:        YES - QUANTITY      	  NO    MAGNEHELIC GAGE KIT

HOUSING(s) DESIGNATION (SIZE)    1x1    1x2    1x3    2x2    2x3     2x4     3x3     2x5     3x4

SPECIAL, Describe

- ACCESSORIES

YES  NO	DESCRIPTION	YES  NO	DESCRIPTION

Pneumatic Exhaust Silencers – STANDARD	          Slide Gate(s)  10”___   12”___  14”___   Other___

Pneumatic Compressed Air Valve Kit - Size (1.5" STD):                  Sprinkler Head Sets

Drum Lid Kits(s) – 55 gal (1) 30 gal ___ 20 gal ___ Quantity:                  Drum(s) –Quantity:

Structural Upgrade, Describe

Hopper Access Door(s) - Quantity:                                                              Special Paint Color, Describe

Location:    Front        Rear 		     Note: Paint Chip Required

SPECIAL INSTRUCTIONS: This order includes an additional 5% for a competitive project with 2007 pricing.  This unit will be mounted outdoors for the location in the Gulf Coast area.  Our contractor will mount the unit to concrete piers.  Contact Info: Chevis Necaise @ #228.868.6057 and fax @ #228.868.6060.