AMTECH CARTRIDGE DUST COLLECTOR

Model AV-4

IMPORTANT READ THIS MANUAL BEFORE INSTALLATION, OPERATION OR SERVICE.

By nature and variety of dusts, it is impossible to list all potential hazards related to dust control equipment or systems. Therefore, it is imperative the application and use of this equipment be discussed with an Amtech distributor, this manual be read in it’s entirety and all personnel involved with this equipment be instructed to comply with the statements pertaining to safety.

- INSTALLATION

- OPERATION

- SERVICE

# Table of Contents

PRECAUTIONARY STATEMENTS								3

INTRODUCTION										3

HOOD AND DUCT DESIGN								3

EXPLANATION OF OPERATION								3

INITIAL INSTALLATION CONSIDERATIONS							4

INSPECTION										4

INSTALLATION										4

COMPRESSED AIR SUPPLY								5

ELECTRICAL/CONTROLS									5

PRE-START UP										7

FILTER INSTALLATION									7

START UP								         		7

SHUT DOWN										7

MAINTENANCE SAFETY									8

MAINTENANCE PROCEDURES								9

CARTRIDGE FILTER REPLACEMENT							10

TROUBLE SHOOTING CHART								11

WARRANTY STATEMENT									13

PARTIAL PARTS LIST									14

PRECAUTIONARY STATEMENTS

APPLICATION OF AMTECH CARTRIDGE DUST COLLECTORS

1. Due to potential fire hazards, do not mix combustible materials with material that would be a potential source of ignition.

Examples of Combustible Materials:

Wood Dust

Paper Dust

Lint from fabric or buffing wheels

Grinding dust from painted surfaces

Aluminum or magnesium dusts

Examples of Potential Ignition Sources

Grinding dust from ferrous metals

Hot ash or sparks from any source

2. Unless the equipment was originally designed for collection of explosive material and proper disclaimer on record this equipment must not be used for the collection of any materials where there is a risk of explosion. Pressure relief vents or explosion vents must not be applied to the equipment or adjoining systems.

3. Equipment location, installation and operation must comply with all National and Local Fire Codes. When in doubt contact proper authorities.

4. The electrical installation must conform to all local codes and the National Electric Code.

5. Workers and operators are to be instructed to keep burning objects, such as cigarettes, safely away from inlets leading to the equipment.

6. All personnel involved with the use of this equipment must comply with the statements pertaining to worker safety as noted in this manual.

Introduction

AMTECH cartridge dust collectors are designed to filter out solid particulate and dusts such as

Weld fume and grinding dust. The cleaned air is then returned to the work space to eliminate the need to exhaust treated air. The collector can be suspended from the roof structure, supported from legs or placed directly on the floor. A dust drawer is available for floor mounted installations. With suspended or leg supported installations a hopper is available for dust removal.

Once the unit is mounted and ductwork installed, the connection of electrical power and compressed air complete the installation.

Note: If the unit has the optional fire suppression system please refer to the Fire Trace Manual and Smoke Detector manual for maintenance information.

Hood & Duct Design

The hood and duct design is critical to assure an effective dust/fume collection system. A text such as “Industrial Ventilation” A Manual of Recommended Practice, (25th Edition is current at time of this writing) is available from The American Conference of Governmental Industrial Hygienists. This text is an excellent guide for hood and duct design. Should additional assistance be required contact your AMTECH Distributor.

Explanation of Operation

During normal operation, contaminated air is pulled through side section of the cartridge collector cabinet. The cabinet design distributes the contaminated air uniformly across the vertically arranged filter cartridges. A portion of the dust will collect on the surface of the cartridge media as the dust free air passes through the media, through the vertical venturi, into the horizontal clean air duct and to the blower for return to the work space. The dust that collects on the cartridge media will be repelled into the downward air flow by the reverse jet pulse cleaning system. This is controlled by a solid state timer. At prescribed times a brief burst of compressed air will be released to a row of cartridge filters, fired upwards through the vertical venturi, into the core of the cartridge filter to impact the dust away from the filters surface. The dust is caught by the downward flow and once again moved towards the settling chamber. The hopper or dust drawer of the AMTECH Collectors contains no airflow inlets or outlets. In fact, airflow is never close to the hopper or dust drawer. This eliminates the possibility of re-entrainment of the dust once it gets into these sections of the dust collector cabinets.

Initial Installation Considerations

The location of the unit(s) must be planed to maximize effective operation, service and maintenance. Should questions arise or assistance is needed consult your AMTECH distributor.

After the installation, clearance must be available to service the following components:

1. Filters

2. Fan

3. Valves

4. Controls

5. Dust storage devise such as dust drawer or dust drum.

Structural supports and hangers must be capable of supporting the load of the dust collector plus options and the heaviest load of dust the collector can contain.

Inspection

Upon receipt, the collector and the optional components must be checked for damage or loss incurred during shipping. Damage must be noted on the bill of laden and a claim be filed with the carrier immediately.

Mechanical Installation

Prior to mounting the unit it may be advantageous to remove the cartridge filters to reduce the weight of the collector. Store filters in a safe location. Should the installation require a hopper or dust drawer to be installed on the collector the joining flanges must be sealed to eliminate air leaks. Use silicone or an equivalent high quality sealant.

Note:

Leaks at the flanges of the hopper or dust drawer will cause excessive dust re-entrainment. Be certain no air leaks exist.

Should the unit include a Leg/Hopper assembly? Position it in the planned installation location. Assemble the leg kit to the hopper as illustrated on the drawing, last page of manual. Anchor the Leg/Hopper assembly to the concrete floor using 3/4” tapered anchor bolts, 1 per anchor pad for a total of 4 each, tapered anchor bolts.

Use silicone or equivalent high quality sealant on the flanges and place the collector on the Leg/Hopper assembly. Using the supplied bolts, nuts and washers secure the collector to the Leg/Hopper assembly. A drift pin or alignment tool will aid in hole alignment.

Should the collector include a Cradle/Hopper assembly for suspension from overhead, locate and attach the Cradle/Hopper assembly to adequate overhead structure. Be certain the overhead structure and suspension method is capable of easily handling the total weight of the collector, all attached components/options and the maximum added weight due to dust load.

Should the collector include a factory installed dust drawer, position the collector in the planned location and secure it in place.

Note:

Should question arise concerning total weight, consult your Amtech Distributor or the Amtech Factory.

Compressed Air Supply

The compressed air supply is used to reverse jet pulse the dust coated cartridge filters. A 1.5” diameter (minimum) dedicated supply with 80-90 PSI is required. If a 1.5” supply is not available a 30 gallon accumulator tank must be installed with a 1.5” line from the tank to the collector manifold. The largest supply line available, up to 1.5” should feed the accumulator tank. The unit has a 2” connection.

The air supply line to the accumulator tank must include water, oil and particulate filtration. Water and/or oil in the compressed air will reduce the effectiveness of the reverse jet pulse cleaning, destroy the cartridge filters and cause excessive differential pressure across the filters resulting in greatly reduced air flow along with premature filter replacement.

Note:

The air line must be free of oil and water. Oil and/or water will destroy cartridge filters.

A 160 PSI gage must be installed to monitor air pressure. Prior to the final connection of the air line to the collector manifold, the air line should be purged. This will remove debris that could damage the valves and block the nozzles in the blow pipes.

Electrical / Controls

Note:

All of the electrical installation must be performed by a qualified electrician and in accordance with the local codes.

The blower motor operates with 208-230/460 volt, 60 cycle, and 3 phase electrical power unless specified otherwise with the equipment order. Electrical power is connected to the J-box on the blower section of the collector. Inside the J-Box is a decal that confirms the voltage the motor was set up for at the factory. Should this need to be changed to the other voltage listed above, the motor will have to be rewired in accordance to the data label on the motor. Access the motor from the blower door of the collector.

The blower motor will need to be energized through a motor starter with over load protection. The electrical components must be sized and selected in accordance to the national electric code.

Nominal Full Load Amperes are as follows:

Voltage	208		230		460

Horse Power

3			11		9.6		4.8

5			17.5		15.2		7.6

7.5			25.3		22		11

10			32.2		28		14

15			48.3		42		21

The blower is designed to rotate clock wise when viewed from the motor side. If the blower is running in reverse, the air volume will be approximately 1/2 the designed air volume. Also, excessive noise will be generated. Once the motor is wired, energize the blower motor for a brief instant (“JOG”). Check the rotation and if it is in reverse, switch any two input wires of the 3 phases, (T1, T2, and T3).

When the reverse jet pulse cleaning system is initiated, a sequential timer controls the air solenoid valves, releasing a brief burst of compressed air backwards through the filters to expel the collected dust off the filter cartridges and down towards the settling area. This process can be a continuous cycle during normal operation by wiring the sequential timer in parallel with the motor starter coil.

The sequential timer can be activated

By monitoring differential pressure across the filters and energizing the timer at a predetermined set point. The timer will continue the reverse jet pulse cleaning until differential pressure is reduced to a predetermined pressure.

An optional microprocessor based sequential timer is available. The microprocessor can be set up to initiate the sequential timer by monitoring filter differential pressure or real time. This is the most versatile control available.

Note:

A manual that details the operation of each control is available under separate cover. Also, a copy of the control manual is supplied within the control enclosure.

The reverse jet pulse control must be mounted in a safe, accessible location were it can be easily monitored as required. Once mounted, the solenoids on the valves must be wired to the control. As a general rule, the closest valve to the filter access door is valve number 1 and the farthest valve from the door is the last valve of the collector.

The valves operated on 115 volts, 60 cycle, and single phase power.  The power required is 22 watts. The terminal block on the sequential timer board is labeled for the input power and the valve outputs.

The pulse control requires 115 volts, 60 cycle input power. Power consumption is less than 50 Watts. Collectors that are supplied with reverse jet pulse controls that include a “Cycle Down” feature must be wired with a dedicated and continuous 115 volt circuit. These controls cannot be wired in parallel to the motor starter transformer.

Note:

Reverse jet pulse controls with “Cycle Down” feature must be wired with a continuous 115 volt supply. The control must not be wired in parallel with the fan motor starter.

The controls that monitor filter differential pressure require pneumatic hoses to be connected. Beside the filter access door are 2 ports for connecting the hose. They are labeled “HIGH” and “LOW”. On the control enclosure are 2 ports also labeled “HIGH” and “LOW”? Inter connect these ports with air tight tubing.

Pre-Start Up

Turn the fan “ON” for a brief instant (JOG) and check rotation. Rotation must be clockwise when viewed “OVER THE MOTOR” from the discharge side. If the rotation is correct start motor.

Assure that rotary air locks, screw conveyors or any other rotating components are rotating the correct direction.

Check to assure that air leaks do not exist at the seams of any field assembled cabinet components such as hoppers, dust drawers, plenums, filter cabinets, Etc.

Check the compressed air system for leaks. Confirm 80 PSI minimum air pressure and 90 maximum air pressure.

Assure the compression couplings of the pulse valves are tight.

Energize the sequential timer and set on time for .15 seconds and off time for 30 seconds.

Check each valve to assure each pulses as required.

Check each valve for leaks. It is normal for the bleed air port to release a burst of air at each pulse.

Check adequacy of air supply by assuring no less than 30% drop in pressure during pulse.

Filter Installation

Should the filter be shipped loose from the collector they must be installed as follows prior to start up?

Be sure the horizontal flange around the venturi is clean. With care not to damage filter cartridge place gasket side down on flange. Rotate filter slightly to assure no binding and proper location on the flange.

Most AMTECH dust collectors use two filters, stacked vertically on each venturi. Position second filter directly on top of first filter, gasket side down and centered vertically with lower filter.

Place filter cap with gasket side down on top of the top filter cartridge and centered on opening. Turn “T” handle, clockwise, down against filter cap so that the dimple penetrates the threaded bore of the “T” handle. Continue to rotate “T” handle until gaskets are approximately 30% compressed.

Start Up

New filters should be properly pre-conditioned before start up. Factory pre-conditioned filters are available from AMTECH. Filters not pre-conditioned can be conditioned in the field. Please contact your AMTECH Distributor for assistance.

Start system fan and confirm the designed air volume and actual air volume are within 10%. If the air volume is more than the designed volume adjustments should be made to reduce the volume to the designed volume.

If air volume is low, and the contaminate is not being captured, adjustments will need to be made. Consult your AMTECH Distributor.

Apply compressed air to the manifold. Turn the reverse jet pulse control on. Apply power to other auxiliary equipment as required.

COMMENTS REGARDING FILTER DIFFERENTIAL PRESSURE DURING OPERATION:

Depending on dust loading and Air-To-Cloth Ratio, reaching equilibrium of filter differential pressure will vary from a few hours to many days. Low dust loading will normally develop 2-3”, with 3-5” normal loading and 5 - 8” with high loading.

Low dust loading typically show a steady level of differential pressure with very little fluctuations once equilibrium is reached. By contrast, heavy loading can produce

Significant “Ups and Downs” in operating differential pressure.

Do make immediate “Off-Time” time reductions on the timer board dial if significant increases in operating differential pressure are discovered. However, if differential pressure drops do not be too quick to increase “Off-Time”, and then only in small steps.

Note:

A critical step in start up is to reach an acceptable operating equilibrium point. This must be reached gradually in order to not damage the filters by blinding. While achieving equilibrium, you want to clean the filters more often than required instead of not often enough. Gradually and tentatively increase valve “Off Time” until equilibrium is reached. Also, making notes and recording the results will help gage the effectiveness of various AMTECH filters and filter pretreatment. Should questions arise contact your AMTECH distributor.

Shutdown

Shutdown consists of shutting down the blower motor. With systems that include a “Cycle Down” feature the reverse jet pulse cleaning will be activated. This will clean the filter cartridges while the unit is off line, for a preset amount of time. Once the cleaning cycle is complete the collector is ready to be energized when needed.

Caution:

Off line cleaning can cause pressure waves to feed back through the inlet of the collector and the attached duct work. Precautions might be needed to prevent dusting.

Maintenance Safety

Care with the design of AMTECH collectors has minimized safety hazards for the maintenance and production personnel.

Caution:

Personnel involved with the AMTECH collector must be familiar with the operation and the information in this manual.

1. Only competent, safety conscious personnel should have access to the area.

2. Work crews should consist of 2 or more people.

3. All areas below the collector must be “OFF-LIMITS” when overhead work is performed.

4. Objects lifted by crane or hoist must be securely fastened and carefully handled to prevent injury.

Maintenance Procedures

With sound periodic and routine maintenance programs you will receive a long service life from your AMTECH collector. Schedules should be changed as a result of experience, determined after a reasonable period of operation.

Routine maintenance consists of the following:

1. Observe the filter differential pressure at least once every 8 hours of operation. Each application will vary. Refer to “Comments Filter Differential Pressure during Operation” at the beginning of page 7.

2. Assure the collected dust is removed from the dust storage container as required.

3. Assure the predetermined cleaning schedule is proper to maintain pressure differential equilibrium.

4. Confirm the reverse jet pulse cleaning takes place at the predetermined schedule.

5. Observe compressed air supply to confirm pressure of 90 PSI.

6. Perform general house keeping on collector and surrounding area.

Periodic maintenance consists of the following:

1. Replace filters when reverse jet pulse cleaning is no longer effective to reduce differential pressure to the normal operating range.

2. Clean the internal parts of the reverse jet pulse control with a quality electrical cleaning chemical.

3. Clean the internal components of the fan control.

4. Remove any accumulated dust from the pressure port that is connected to the Magnehelic Gage or Reverse Jet Pulse Control or both. This is located inside the dust collector on the dirty air side.

5. Replace the cartridge filter caps after every 4th filter change or before if failure of gasket seal occurs.

Note: Be certain the compressed air is off and the pressure relieved before servicing any components that contain compressed air.

6. Follow the manufacturer’s maintenance schedule for the compressed air filters.

7. Tighten the couplings of the valves for the reverse jet pulse cleaning.

8. Remove any moisture that has accumulated in the compressed air manifold and accumulator.

9. Inspect and clean diaphragm valves. A thorough cleaning normally rectifies operational problems with valves; however any worn or damaged parts are to be replaced. Use the following procedure to inspect and repair valves:

A. Main Diaphragm

1. Switch off air supply and drain the system

2. Unscrew the main diaphragm cover bolts and remove the valve cover.

3. Inspect the spring and diaphragm for dust and damage. Remove dust with water and replace damaged parts with parts kit # 200149 for 1” valves and 200150 for 1.5” valves.

4. Replace valve cover and valve cover bolts.

B. Solenoid Diaphragm

1. Switch off air supply and drain the system.

2. Unscrew the bonnet bolts and remove the bonnet.

3. Inspect the spring and diaphragm for dust and damage. Remove dust with water and

replace damaged parts with part kit # 200151 for 1” valves and 200152 for 1.5” valves.

4. Replace the valve bonnet and valve bonnet bolts.

C. Solenoid Coil

1. Switch off air supply and drain system

2. Apply proper voltage to the coil and listen for a pronounced “Click” as the pole moves.

3. If a pronounced “Click” occurs and the valve does not function follow instructions (B) Solenoid Diaphragm above.

4. If the “Click” is not heard, replace solenoid with part # 200153 for 1” valves and

200154 for 1.5” valves.

10. Check and replace, if necessary the access door gaskets and dust drawer gaskets if applicable.

Cartridge Filter Replacement

Note: Depending on the contaminant being collected, it is advised to wear a dust respirator when handling dirty filters.

Turn the “T” handles counter-clockwise until clearance is obtained above the cartridge filter. Remove top cover from top of filter. Slide plastic bag over filter and pull it down to cover top filter and remove. Cover the bottom filter with a plastic bag and remove. Repeat this with all filters.

Note: Discard filters according to all local codes and regulations. Please help protect the environment.

Follow filter installation instructions on page 6 to replace filters.

TROUBLE SHOOTING GUIDE

SYMPTOM			POSSIBLE CAUSE        		REMEDY

Blower does not start	a. Open electrical supply circuit		Trace circuit back from motor and

correct interruption

b. Blower motor not wired for 		Rewire motor within motor box for				     available voltage			proper voltage per motor data label

Blower motor starts but	a. Incorrect overload protection 		Replace overload protection with

does not continue 	   installed				correctly sized components

operating

b. Loose or incorrect termination of		Check all termination’s of motor

motor wiring				wiring

c. Incorrectly sized wire for motor 		Rewire motor circuit with proper

load					wire size

Dust discharge from	a. Filter cartridges not properly		Reinstall filters according to

collector outlet		   installed				instructions on page 6

b. Damaged filter cartridge		Locate and replace damaged

filter(s)

c. Damaged filter cap(s)			Replace damaged filter cap(s)

d. Worn filter cap				Replace all filter caps

e. Loose filter clamping “T” handle		Tighten loose “T” handles

Insufficient airflow	a. Blower rotating backwards		Check blower rotation. Blower

should be rotating clockwise when									looking down over motor. Refer

to page 5 under ELECTRICAL

for changing rotation direction.

b. Collector not sealed properly		Check all access panels, doors,

dust drawers and dust

removal/container connections

to assure air tight.

c. Blower exhaust area blocked		Check exhaust area for blockage

and eliminate all material that 									cause restrictions.

d. Filter Cartridges need 			Remove and replace filter

to be replaced.				cartridges per instructions on									page 6.

TROUBLE SHOOTING GUIDE (CONTINUED)

SYMPTOM		POSSIBLE CAUSE			REMEDY

e. Compressed air volume			Increase available air volume.

inadequate.				Refer to pages 4 and 5.

f. Compressed air pressure 		Increase air pressure. Refer

inadequate.				to pages 4 and 5.

g. Compressed air 			Eliminate source of contamination

contaminated with oil or			and purge compressed air line

water.

h. Pulse cleaning not working.		Check red “power on” LED

to confirm input power.

Check control switch to assure

it is positioned as required

(on demand or manual). Refer

to control manual for more detail.

i. Pulse cleaning not set up		The “on-time” and “off-time” must

as required.				be set to optimize filter pressure 									differential equilibrium. Refer to 									pages 6 and 7 of this manual and

to the reverse jet pulse control 									manual for additional detail

j. Reverse jet pulse valves not 		Clean, repair or replace valves.

operating.				Refer to page 8.

WARRANTY STATEMENT

2 Year Limited Warranty

Items not covered with this warranty are filters and ductwork, wiring and installation not supplied by Amtech L.C.

Amtech L.C. warrants that all new Amtech L.C. dust collectors/air cleaners are free from defects in material and workmanship under normal use and service.  Amtech L.C. will remedy any such defects if they appear within 24 months from the date of installation, subject to the terms and conditions of this 2 year Limited Warranty stated below.

1. This Limited Warranty is granted by Amtech L.C.  127 Franklin Road, Russellville, KY 42276.

2. This warranty shall extend to any owner who has purchased the equipment other than for the purpose of resale.

3. All components manufactured by Amtech L.C. are covered by this Limited Warranty with the exception of filters and components not manufactured by Amtech L.C. i.e. fire suppression system, electrical or electronic equipment such as motor starters, pulse controls and valves. Those items not manufactured by Amtech L.C. have a one year manufacturer’s Limited Warranty.

4. If within the Limited Warranty period any Amtech L.C. unit or component requires service, it must be performed by an Amtech L.C. service representative or Amtech L.C. distributor. Amtech L.C. will not pay shipping charges or labor charges to remove or replace such defective parts or components.  If the part or component is found by inspection to contain such defects in material and workmanship, it will be either repaired or exchanged free of charge and returned freight collect.

5. In order to obtain the benefits of this 2 year Limited Warranty the owner must notify the distributor or Amtech L.C. in writing of any defect within 30 days of its discovery.

6. This Limited Warranty does not apply to any part or component that is: damaged in transit or when handling; has been subject to misuse, neglect or accident; has not been installed, operated and serviced according to Amtech L.C.’s instruction; has been operated beyond the factory rated capacity; or altered in any way that would affect its performance. There is no Limited Warranty due to neglect, alteration or ordinary wear and tear. Amtech L.C.’s liability is limited to replacement of defective components and does not include the payment of the cost of labor charges to remove or replace such defective components or parts.

7. Amtech L.C. will not be responsible for loss of use of any product; loss of time, inconvenience, or any other indirect, incidental or consequential damages with respect to personal property, whether as a result of breach of warranty, neglect or otherwise. Some states do not allow the exclusion or limitation of incidental or consequential damages, so the exclusion or limitation in the preceding sentence may not apply to you.

8. This Limited Warranty give you specific rights, and you may also have other rights that vary from state to state.

9. Any warranty work will be performed within a reasonable time, usually within 60 days after notice of defect and delivery to the Amtech L.C. factory, subject to delay beyond Amtech L.C.’s control.

10. Any warranty by Amtech L.C. of merchantability, fitness for use or any other warranty (express, implied or statutory), representation or guarantee other than those set forth herein, shall expire at the expiration date of this express limited warranty.  Some states do not allow limitations on how long an implied warranty lasts, so the limitation in the preceding sentence may not apply to you.

11. Amtech L.C. reserves the right to make changes in the design and material of its products without incurring any obligation to incorporate such changes in units completed on the effective date of such change.

REPLACEMENT PARTS LIST

AMTECH MODEL AV-4, 7.5HP, 18” 50%

PART DESCRIPTION				PART NO.		QTY. PER UNIT

Filter, Cartridge 351D91A3292			2493			4 each

Plate, Filter Cap with gasket			1222			4 each

“T” Handle, Filter Clamp			1224			4 each

“T” Handle, Access Door Latch			1023			5 each

Gasket, Door Seal				1214			5 meters

Valve, 1.5” Double Diaphragm			1221			2 each

Motor, 7.5 HP 3 Phase, 3500 RPM, TEFC		1040			1 each

Fan Wheel 18” 50% Width, CW, 			2565			1 each

Inlet Cone, 18”					1054			1 each

TURBO Pulse Control				1513			1 each