## SCOPE
SCOPE OF WORK for installation of HDEV5 Laser Welding Exhaust System
Background:
Robert Bosch, LLC has need for a vacuum system for the collection of welding smoke and particulate
for seven (7) laser welding machines and one (1) tray exhaust machine.
Two (2) additional pick up points for tray cleaning/blow off stations will also be added.
Design Features:
1. Minimum air velocity in the exhaust piping of 15-20 M/sec (2,953 - 3,937 FPM)
2. Pressure of 15000 pa (2.2 PSI)
3. 800 cubic meters/hr (471 CFM) flow.
4. 200 mbar vacuum
5. Continuous Duty operation
6. Remote On/Off
7. No exhaust in clean room (vacuum to exhaust external of room)
Scope of Work:
Contractor to furnish all equipment (vacuum system and tubing), labor, lift equipment, piping/tubing and required accessories for complete system installation.
(Bosch will set vacuum unit in place, provide compressed air and wire to vacuum unit).
Contractor to provide installation of piping/tubing, fittings, elbows, blast gate dampers, tube hangers, tube laterals, couplings
as required to drop piping/tubing to identified equipment locations.
Contractor to quote motor starter, disconnect on vacuum unit if available.
Contractor to provide start up, training and testing of vacuum system after installaton is complete.
Contractor to provide system diagram, vaccum unit layout with dimensions and pipe/tubing layout.
Notes:
All to be performed during normal working hours (No overtime).
All contractors performing work on site must be Lowcountry Safety Council (Bosch specific) trained and certified.
Quotes to itemized for materials, labor and rental equipment.
Equipment layout drawings have or can be provided.
Questions:
Contact: Herb Redick
Office: 843-760-7705
Cell: 843-323-1836
herb.redick@us.bosch.com