Customer:	 Wake Tech

9101 Fayetteville Rd.

Raleigh, NC 27603-5696

Contact:	 Russell A. Wahrman

Phone: 	 919-866-5152

Email:		 rawarman@waketech.edu

Date:  1/14/11

Project #: Unit Start-up

Sales Order #:

Serial #: various

Model #: WB-3000

OE Crew:  Bill Boisvert

SCOPE OF PROJECT:        (Installation) – Service – Warranty – Demo – Delivery - Engineering

Completed Start-up on the following Welding Booths.

- Booth # 1

  - SN: 104607

  - Gauge Reading – 0.7”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

- Booth # 2

  - SN: 104609

  - Gauge Reading – 0.6”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

- Booth # 3

  - SN: 104616

  - Gauge Reading – 0.7”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

- Booth # 4

  - SN: 104613

  - Gauge Reading – 0.6”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

- Booth # 5

  - SN: 104612

  - Gauge Reading – 0.5”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

- Booth # 6

  - SN: 104610

  - Gauge Reading – 1.0”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

- Booth # 7

  - SN: 104611

  - Gauge Reading – 0.8”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - No Lights

- Booth # 8

  - SN: 104608

  - Gauge Reading –1. 0”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

- Booth # 9

  - SN: 104615

  - Gauge Reading – 0.8”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

- Booth # 10

  - SN: 104614

  - Gauge Reading – 0.6”WC

  - Rotation Correct

  - All controls functioned as designed

  - Left with E-Stop pushed

  - Work lights operational

Note:

Air pressure to the unit should be between 85 and 95 PSI.  Pressure above 95 PSI may damage the filter media.  Air needs to be dry, as moisture will also shorten the filter life.

Note:

Two lights are still on order as well as all 20 welding curtains .

Feel free to call with any concerns or problems.

Thanks,

Bill Boisvert

Bill Boisvert - Cell (919) 971-3910

Project Manager – Avani Environmental Intl.

E-mail bboisvert@avanienvironmental.com

CUST0MER REMARKS: _____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________