Mr. Tokso Pak

Altec, Inc.

1550 Aerial Ave.

Creedmoor, NC 27522

Tokso,

After our discussion with you yesterday (1/6/11) Bob and I completed the following actions:

- We set the Code 04 to 0.02 kPa on all five units. (1 kPa is approximately 4 inches of water gauge.)

- We set the Code 05 to 2.0 kPa on all five units.

- We set the Code 08 to 2 on all five units.

This will cause the units to pulse off line for 2 cycles at unit shut down.

Unit #2 has a broken STOP button and if the unit is shut down by opening the Main Disconnect the unit will not pulse as intended.

We still recommend that the units be pulsed off line for 30 minutes once a month, by using the manual switch on the front of the control panels.

Bill Boisvert

Bill Boisvert, Project Manager

Avani Environmental

Cell: 919-971-3910

Office: 919-570-2862 x219

E-mail: bboisvert@avanienvironmental.com