## Western Precept
Western Precept
Floor 3 |  |  | Floor 2 |  |  |  | Floor 3 | Floor 2 | Western Precept
Location | Duct Size | CFM Required | Location | Duct Size | CFM Required | Total Needed: | 12937.2531 | 7155.8499 | 20093.103
Line 1 Oddball Bin Tripper | 8 | 1396.2634 | Bin Dump | 8 | 1396.2634 | Recorded: | 6460 | 3400 | 9860
Line 1 Oddball Bin Tripper | 8 | 1396.2634 | Farrel Mixer | 6 | 785.3982 | Difference: | -6477.2531 | -3755.8499 | -10233.103
Dust Dropper #1 | 8 | 1396.2634 | Farrel Mixer | 8 | 1396.2634
Line 1 Scrap Scale | 8 | 1396.2634 | Farrel Mixer | 8 | 1396.2634
Bag Feed | 5 | 545.4154 | Farrel Mixer | 6 | 785.3982
Bin Dumps | 6 | 785.3982 | Farrel Mixer | 8 | 1396.2634 | Static Pressure measured at 2.25" SP before collector from floor 2
Line 1 Breaker | 6 | 785.3982 |  | Total: | 7155.8499
Line 1 Breaker | 6 | 785.3982 |  | Recorded: | 3400
Line 1 Breaker | 6 | 785.3982 |  | Difference: | -3755.8499 | Static Pressure measured at 2.50" SP before collector from floor 3
Trolley Conveyor | 6 | 785.3982
Trolley Conveyor | 4 | 349.0659
Trolley Conveyor | 4 | 349.0659
Trolley Conveyor | 4 | 349.0659
Trolley Conveyor | 4 | 349.0659
Trolley Conveyor | 4 | 349.0659
Trolley Conveyor | 4 | 349.0659
Scrap Bin Tipper | 6 | 785.3982
| Total: | 12937.2531
| Recorded: | 6460
| Difference: | -6477.2531
FPM Desired | 4000

## Evo Collector
EVO Collector
Floor 3 |  |  | Floor 2 |  |  |  | Floor 3 | Floor 2 | EVO Collector
Location | Duct Size | CFM Required | Location | Duct Size | CFM Required | Total Needed: | 4799.6554 | 6544.9847 | 11344.6401
Bin Dump | 6 | 785.3982 | Farrel Mixer | 8 | 1396.2634 | Recorded: | 5620 | 3935 | 9555
Bin Dump | 6 | 785.3982 | Farrel Mixer | 8 | 1396.2634 | Difference: | 820.3446 | -2609.9847 | -1789.6401
Trolley Station 7 | 4 | 349.0659 | Farrel Mixer | 8 | 1396.2634
Trolley Station 2 | 5 | 545.4154 | Regrind Hopper | 6 | 785.3982
Trolley Station 6 | 4 | 349.0659 | Regrind Hopper | 6 | 785.3982 | Static Pressure measured at 7.50" SP before collector from floor 2
Trolley Station 1 | 5 | 545.4154 | Conveyor Transfer | 6 | 785.3982
Trolley Station 1 | 4 | 349.0659 |  | Total: | 6544.9847
Trolley Station 4 | 5 | 545.4154 |  | Recorded: | 3935 | Static Pressure measured at 10.00" SP before collector from floor 3
Trolley Station 3 | 5 | 545.4154 |  | Difference: | -2609.9847
| Total: | 4799.6554
| Recorded: | 5620
| Difference: | 820.3446
FPM Desired | 4000

## South Sly
South Sly
Floor 1
Location | Duct Size | CFM Required |  | South Sly
Mottle Mill | 8 | 1396.2634 | Total Needed: | 5585.0536
Mottle Mill | 8 | 1396.2634 | Recorded: | 9035
Mottle Mill | 8 | 1396.2634 | Difference: | 3449.9464
Mottle Mill | 8 | 1396.2634
| Total: | 5585.0536
| Recorded: | 9035 | Note: South Sly connects to Western Precept and EVO on floor two for backup.
| Difference: | 3449.9464
FPM Desired | 4000
Static Pressure measured at 7.00" SP before collector.

## Line 3 Sly
Line-3 Sly
Floor 3 |  |  | Floor 2 |  |  | Floor 1 |  |  |  | Floor 3 | Floor 2 | Floor 1 | Line-3 Sly
Location | Duct Size | CFM Required | Location | Duct Size | CFM Required | Location | Duct Size | CFM Required | Total Needed: | 5366.8874 | 5061.4548 | 13613.5682 | 24041.9104
Bin Dump | 5 | 545.4154 | Farrel Mixer | 8 | 1396.2634 | Bin Dump | 7 | 1069.0142 | Recorded: | - | - | - | 15954
Bin Dump | 4 | 349.0659 | Farrel Mixer | 6 | 785.3982 | Bin Dump | 7 | 1069.0142 | Difference: | - | - | - | -8087.9104
Weighing Table | 8 | 1396.2634 | Farrel Mixer | 4 | 349.0659 | Hood Line 3 | 8 | 1396.2634
Bulk Bag Feed | 4 | 349.0659 | Farrel Mixer | 4 | 349.0659 | Line 3 Mill | 10 | 2181.6616
Material Feed Blender | 5 | 545.4154 | Line 3 Conveyor | 8 | 1396.2634 | Bin Dump | 6 | 785.3982 | Fan Rated for 22,528 CFM @ 13" SP.
Mixer Feed | 5 | 545.4154 | Line 3 Conveyor | 6 | 785.3982 | Hood Line 3 | 12 | 3141.5927
Mixer Feed | 5 | 545.4154 |  | Total: | 5061.4548 | Line 3 Conveyor | 3 | 196.3495
Mixer Feed | 5 | 545.4154 |  |  |  | Line 3 Conveyor | 3 | 196.3495 | Static Pressure measured at 4.00" SP before collector, 7.00" SP after collector.
Mixer Feed | 5 | 545.4154 |  |  |  | Line 3 Conveyor | 8 | 1396.2634
| Total: | 5366.8874 |  |  |  | Line 3 Conveyor | 8 | 1396.2634
[6 empty] | Grinder | 6 | 785.3982
FPM Desired | 4000 | [5 empty] | Total: | 13613.5682

## Fume Extraction
Fume Extraction
Floor 2 |  |  | Floor 1 |  |  |  | CFM |  |  | Per 4000 FPM
Location | Duct Size | CFM Required | Location | Duct Size | CFM Required | Floor 2 | 14224.4334 |  |  | Diameter (in) | CFM Required
Farrel Mixer - Line 3 Sly | 6 | 785.3982 | Line 3 Hood | 10 | 2181.6616 | Floor 1 | 12304.5712 |  |  | 12 | 3141.5927
Farrel Mixer - Line 3 Sly | 4 | 349.0659 | Line 3 Mill | 12 | 3141.5927 | Total | 26529.0046 |  |  | 10 | 2181.6616
Farrel Mixer - Line 3 Sly | 4 | 349.0659 | Line 3 Hood | 8 | 1396.2634 |  |  |  |  | 8 | 1396.2634
Farrel Mixer - Line 3 Sly | 8 | 1396.2634 | Mottle Mill - South Sly | 8 | 1396.2634 |  |  | FE | 26529.0046 | 7 | 1069.0142
Farrel Mixer - Line 3 Sly | 8 | 1396.2634 | Mottle Mill - South Sly | 8 | 1396.2634 |  |  | L3S | 24041.9104 | 6 | 785.3982
Farrel Mixer - Western Precept | 6 | 785.3982 | Mottle Mill - South Sly | 8 | 1396.2634 |  |  | SS | 5585.0536 | 5 | 545.4154
Farrel Mixer - Western Precept | 8 | 1396.2634 | Mottle Mill - South Sly | 8 | 1396.2634 |  |  | EVO | 11344.6401 | 4 | 349.0659
Farrel Mixer - Western Precept | 8 | 1396.2634 |  | Total: | 12304.5712 |  |  | WP | 20093.103 | 3 | 196.3495
Farrel Mixer - Western Precept | 6 | 785.3982 | [6 empty] | 61064.7072
Farrel Mixer - Western Precept | 8 | 1396.2634 | [6 empty] | 43.44%
Farrel Mixer - EVO Collector | 8 | 1396.2634
Farrel Mixer - EVO Collector | 8 | 1396.2634
Farrel Mixer - EVO Collector | 8 | 1396.2634
| Total: | 14224.4334
FPM Desired | 4000