1E-MAIL TRANSMISSION

EUROVAC

116 Buttermill Ave.

Concord, Ontario L4K 3X7

Tel: 905-738-9255

E-mail: bretter@eurovac.com

| Date: July 24, 2008 | From: Burt Retter |
| --- | --- |
| To: Bob Venezia | Company: IAQ |
| E-mail #: bvenezia@iaqsales.com rsheffergbucknps@sbgcglobal.netley | Pages: |

The following is our quotation for the 5 vacuum systems outlined in your July 22, 2008 e-mail.    The quotations for the Powdered Porcelain lines 1 & 2 are the same and the quotations for the Robot vacuum and Furnace vacuum are the same.

A. Central System

CFM Assumption:

8 technicians vacuuming @ 80 CFM ea. = 640 CFM

Vacuum Assumption:

8" HG to offset a longest run of 400 ft. (it appears that the system could be redesigned to decreas the length of the longest run - this would be a good thing).

From the information provided to us, we recommend the following equipment:

* 40-305222, 3 phase 220 or 480 volt, centrifugal exhauster with 30 H.P. T.E.F.C. motor    capable of producing 730 S.C.F.M. at 8" HG (see attached specs on motor/blower units).

*discharge silencer

* 12" high efficiency cyclonic pre-separator w/55 gallon cannister

*30" x 84" cyclonic filter separator with 2 - 9" x 36" secondary polyester cartridge filters (140 sq ft of filter media) with automatic compressed air pulse jet cleaning.    30 gallon collection canister (see enclosed drawings and specs).

*vacuum relief valve

* electrical control panel for the 30 H.P. motor and the automatic pulsejet cleaning. Includes magnetic starter, overload protection with panel mounted stop/start and remote stop/start capability.

* approximately 560 ft. 2" to 5" 16 to 14 gauge graduated galvanized tubing hung from the beams via beam clamps, threaded rod, and pipe clamps.    The fittings will be “butt fit” and secured with compression couplings.    The 90 degree bends will be 11 gauge to withstand the corrosive nature of porcelain dust

* 28 single hanging or wall mount drops.    The hanging drops are attached to the tubing by 2" flex hose.

IAQ cost for the above is as follows:

| Equipment | $27,178.00 |
| --- | --- |
| Freight ** | 1,600.00 |
| Total | $28,778.00 |

** Freight price is an estimate which may very on ship date

Terms: 1/3 with order and the balance in 30 days.

50-500 Anti-static Shop Cleaning Package with anti-static 1 ½" x 25' vacuum hose,

2 piece aluminum wand, 14" floor tool and crevice tool			$ 175 IAQ cost

B. Powdered Porcelain Line 1 and line 2 quotes

CFM Assumption:

2 technicians vacuuming @ 80 CFM ea. = 160 CFM

Vacuum Assumption:

6" HG to offset a longest run of 80 ft.

From the information provided to us, we recommend the following Eurovac I equipment:

The Eurovac I dust extraction system is an industrial grade system with an induction motor and regenerative blower designed to run all day every day with little or no maintenance.    The combination cyclonic and final cartridge filtration removes 99.93% of the dust up to 3 microns and the automatic compressed air pulse jet cleaning ensures very little maintenance.

* 3 phase, 220 or 440 volt, 10 H.P. regenerative blower set up to produce 200 CFM at 6" HG.

* 10" high efficiency cyclonic pre-separator w/30 gallon cannister

* 18" x 48" cyclonic filter separator    with 15 gallon collection canister. Secondary 8" x 16" cartridge filter with automatic compressed air pulse jet cleaning.

* Control panel including starter, overload protection and step down transformer for the 24 volt control circuit.

* approximately 110 ft. 2" to 3" 16 gauge graduated galvanized tubing hung from the beams via beam clamps, threaded rod, and pipe clamps.    The fittings will be “butt fit” and secured with compression couplings.    The 90 degree bends will be 11 gauge to withstand the corrosive nature of porcelain dust

* 5 single hanging or wall mount drops.    Hanging drops are attached to the tubing by 2" flex hose.

IAQ cost for the above is as follows:

| Equipment | $8,660.00 |
| --- | --- |

You will need 2 of these, one for Powdered Porcelain Line 1 and for one line 2

The above system is mounted on a 4' x 7' painted plywood board.    If you want it mounted on a stand, IAQ’s extra cost is $610.

Freight would be approximately $1800 if all four 10 HP systems are shipped at the same time.

Terms: 1/3 with order and the balance in 30 days.

50-500 Anti-static Shop Cleaning Package with anti-static 1 ½" x 25' vacuum hose,

2 piece aluminum wand, 14" floor tool and crevice tool			$ 175 IAQ cost

C. Robot vacuum and Furnace Vacuum

CFM Assumption:

2 technicians vacuuming @ 80 CFM ea. = 160 CFM

Vacuum Assumption:

6" HG to offset a longest run of 80 ft.

From the information provided to us, we recommend the following Eurovac I equipment:

The Eurovac I dust extraction system is an industrial grade system with an induction motor and regenerative blower designed to run all day every day with little or no maintenance.    The combination cyclonic and final cartridge filtration removes 99.93% of the dust up to 3 microns and the automatic compressed air pulse jet cleaning ensures very little maintenance.

* 3 phase, 220 or 440 volt, 10 H.P. regenerative blower set up to produce 200 CFM at 6" HG.

* 10" high efficiency cyclonic pre-separator w/30 gallon cannister

* 18" x 48" cyclonic filter separator    with 15 gallon collection canister. Secondary 8" x 16" cartridge filter with automatic compressed air pulse jet cleaning.

* Control panel including starter, overload protection and step down transformer for the 24 volt control circuit.

* approximately 110 ft. 2" to 3" 16 gauge graduated galvanized tubing hung from the beams via beam clamps, threaded rod, and pipe clamps.    The fittings will be “butt fit” and secured with compression couplings.    The 90 degree bends will be 11 gauge to withstand the corrosive nature of porcelain dust

* 6 single hanging or wall mount drops.    Hanging drops are attached to the tubing by 2" flex hose.

IAQ cost for the above is as follows:

| Equipment | $8,905.00 |
| --- | --- |

You will need 2 of these, one for the Robot vacuum and Furnace Vacuum

The above system is mounted on a 4' x 7' painted plywood board.    If you want it mounted on a stand, IAQ’s extra cost is $610.

Freight would be approximately $1800 if all four 10 HP systems are shipped at the same time.

Terms: 1/3 with order and the balance in 30 days.

50-500 Anti-static Shop Cleaning Package with anti-static 1 ½" x 25' vacuum hose,

2 piece aluminum wand, 14" floor tool and crevice tool			$ 175 IAQ cost

Please call me at 1-800-265-3878 est 224 if you have any questions or if you need more information.