| Avani Environmental | Phone: (919) 570-2862 Fax: (919) 570-2863 |
| --- | --- |
| Attention: Mr. Ken Haga | Quote valid through 6/10/2011 for shipment by 8/9/2011. |

We are pleased to offer our proposal for Cincinnati Fan products:

Item #1 – Direct Drive

| ACFM | SP | Temp. | Altitude | Density | Fan RPM | BHP |
| --- | --- | --- | --- | --- | --- | --- |
| 13000 | 12 in.wg | 70 °F | 0 ft | 0.075 lb/ft³ | 1750 | 36.1 |

| Qty | Description | Unit Price | Extended Price |
| --- | --- | --- | --- |
| 1 | Cincinnati Fan HDBI-300, SQ Wheel, Class III, 80% Width, Arrangement 4 Fan is painted “Avani Blue” | $5,935 | $5,935 |
|  | MOTOR: 40 HP, 1750 RPM, 3PH/60Hz/230/460V,TEFC, Premium Efficiency, FM, 324T,1.15 SF,F Insul., 40C Amb.,F1 Box | Included |  |
|  | Drain with Plug & Inspection Door | Included |  |
|  | Shaft Seal | Included |  |
|  | Flanged Inlet & Flanged Discharge | Included |  |
|  | Optional Accessories |  |  |
|  | Discharge Damper-Opposed Blade | $672 | $672 |

Approximate shipping weight (for complete fan as described above) is 1733 pounds (each).

Item #2 – V-belt Drive

| ACFM | SP | Temp. | Altitude | Density | Fan RPM | BHP |
| --- | --- | --- | --- | --- | --- | --- |
| 13000 | 12 in.wg | 70 °F | 0 ft | 0.075 lb/ft³ | 1713 | 35.6 |

| Qty | Description | Unit Price | Extended Price |
| --- | --- | --- | --- |
| 1 | Cincinnati Fan HDBI-300, Class III, SQ Wheel, 85% Width, Arrangement 9 Fan is painted “Avani Blue” | $8,774 | $8,774 |
|  | MOTOR: 40 HP, 1750 RPM, 3PH/60Hz/230/460V,TEFC,Premium Efficiency,FM,324T,1.15 SF,F Insul., 40C Amb.,F1 Box Motor mounting included. | Included |  |
|  | Drain with Plug & Inspection Door | Included |  |
|  | Shaft/Bearing Guard & Belt Guard | Included |  |
|  | Shaft Seal | Included |  |
|  | Flanged Inlet & Flanged Discharge | Included |  |
|  | Fixed Drives, 1.3 Service Factor | Included |  |
|  | Optional Accessories |  |  |
|  | Discharge Damper-Opposed Blade | $672 | $672 |

Approximate shipping weight (for complete fan as described above) is 1974 pounds (each).

Allow 18 working days to ship after receipt of order, or release to manufacturing.

Net 30 Days.  FOB Factory.  Freight not included.  Please issue PO to Cincinnati Fan c/o Todd Air Solutions.  All Cincinnati Fan & Ventilator Company terms and conditions of sale will apply.  When ordering, refer to the Quotation # at the top of this proposal.

Sincerely,

Penny Shue

Todd Air Solutions