Date: 	3/5/08  	     Project#:  	Danaher Inspection	IAQ Crew: Bill Boisvert

Customer:	Danaher Tool Group				Installation:

1228 Isley Drive				Service: X

Gastonia, NC 28053				Warranty:

Repair:

# Inspection Report

Inspected all Absolent units at the Danaher Plant (11 Units).  Findings as follows:

- Headers 625-1 & 625-2, ODR-3000 IAQ # 100076 (No SN)

  - Gauges Ok

  - Gauge reading:

    - 400PA

    - 200PA

    - 400PA

  - 1st Stage filter replaced 12/27/05

  - Pump Breaker off.

  - Unit has 5” of oil in sump

  - Pre-Filter installed, frame, no pad (pad may be in bottom of unit due the frame installed upside down).

  - No spray system seem, no sight glass

- Header 245-1, ODR-3000 IAQ # 100077 (No SN)

  - All gauges are bad, read but do not return to “0”

  - Gauge Readings

    - 400PA

    - 200PA

    - 1800 PA

  - Fan control not functioning correctly, fan will not shut off from switch.

  - Pre-Filter installed – Pad dirty

  - Spray system with filter installed, has sight glass

  - Found pump floats stuck- cleaned working correctly

- Header 245-2, ODR-3000, IAQ # 100078 (No SN)

  - Header removed for repair

  - No Power to Absolent

  - Gauges all on “0”

  - Internal Spray system.

  - Absolent pump is piped back into unit but does not connect to anything.

  - No Pre-filter installed.

  - Two door clamps are broken.

- Headers FX-3Z & FX-4Z plus two grinders ODR-3000 SN: 20040348

  - Gauges appear OK

  - Gauge Readings

    - 2200PA

    - 200PA

    - 200PA

  - Unit will not shut down from control switch

  - Two door clamps will not close due to interference with control cabinet.

  - Oil pump is not connected to anything and needs to at lease have a valve installed. (Turned off breaker)

  - No Pre-Filter

  - No Spray system or Sight Glass

- ODR-3000, SN: 20020056

  - Frequency Drive not functional and is by passed.

  - Found unit running backward, corrected

  - Spray System with filter and sight glass – operating

  - 1st stage gauge is half full of oil (400PA).

  - 2nd stage appears OK (400PA).

  - HEPA not reading (0PA).

  - No Pre-Filter

Header numbers for the remaining unit not recorded, units are all in first room from left to right, when facing units.

- ODR-3000 IAQ # 100080 (No SN).

  - Gauges OK

  - Gauge Readings

    - 500PA

    - 200PA

    - 100PA

  - Pump floats appear to be stuck, could not check due to very high oil level in bottom of unit.

  - Bottom of unit over ½ full of oil.

  - Spray system with filter and sight glass, not working due to pump floats not working.

  - No Pre-Filter Installed

- ODR-3000, IAQ # 100081 SN: 20001221

  - Gauges OK

  - Gauge Readings

    - 200PA

    - 400PA

    - 900PA

  - Frequency Drive OK

  - Spray system with filter and sight glass, working

  - Pre-filter installed

  - Oil level above top of sight glass

- ODR-3000, IAQ # 100082, SN: 20010521

  - Gauges OK

  - Gauge Readings

    - 400PA

    - 400PA

    - 300PA

  - Pump Breaker is off. Runs fine when turned on.

  - Spray System with filter and sight glass

  - Pre-filter installed

  - Oil level above top of sight glass

- ODR-3000, IAQ # 100083

  - Gauges OK

  - Gauge Readings

    - 400PA

    - 200PA

    - 100PA

  - Pump Breaker is off. Runs fine when turned on.

  - Spray System with filter and sight glass

  - Pre-filter installed

  - Oil level above top of sight glass

- Two ODF-1000’s

  - Both have HEPA’s maxed out

  - Both have 1st stage reads of 0PA