| Description | November 20, 2008 |
| --- | --- |

| Job Description: | Industrial Air Quality |  | Chicago Blower Sales - North Carolina |
| --- | --- | --- | --- |
| Reference: | Bob Venezia |  | David Redman |
| Fan Type: | Industrial Radial Bladed Fans |  | Phone: (704) 788-6893 |
| Fan Model: | Design 39 SQI SW |  | Fax: (704) 788-7057 |
| Fan Size: | 15 |  | e-mail: cbsnc@vnet.net |
| Fan Width: | 100% |  |  |

| Performance |  |  |  |  |  | Values are in accordance with AMCA Standard 210 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Volume Flow Rate (CFM) | 5000 |
| --- | --- |
| Static Pressure (IN. WG) | 12 |
| Density (LB/FT³) | 0.072 |
| Temperature (°F) | 70 |
| Altitude (FT) | 400 |
| Speed (RPM) | 1852 |
| Power Required (BHP) | 15.2 |
| Static Efficiency (%) | 62.2 |
| Outlet Velocity (FT/MIN) | 4065 |
| Damper Opening (%) | N/A |

| Control Type |  | N/A |  |
| --- | --- | --- | --- |
| Outlet Area (FT²) | 1.23 |  |  |

| Maximum Speeds at 70 °F (RPM) |  |
| --- | --- |
| Class 2 Max. RPM | 2181 |