Customer:	 D.H. Griffin

6438 Burnt Poplar Road

Greenville, NC 27409

Contact: Ray	 Freeman / Gary Proctor

Phone:  336-240-2785 / 336-855-7030

Email:	 gproctor@dhgriffin.com

Date:  10/220/11

Project #: N/A

Sales Order #: N/A

Serial #: 073809

Model #: SOU-750

OE Crew: Bill Boisvert

SCOPE OF PROJECT:        Installation – (Service – Warranty) – Demo – Delivery - Engineering

- 10/18/11

  - Visited site and could not repair unit. Need wiring diagram.

  - Loaded unit in truck to bring back to shop.

- 10/20/11

  - Got wiring diagram from Smartvent

  - Rewired unit

  - During inspection found motor cooling fan had some damage due to the fire in the unit. Still moving air so should not be a problem

  - Unit ran sat.

  - Fixed two stripped arm mounting holes.

  - Install wire labels to correspond to drawing.

  - Install new power plug

  - Cleaned unit and reassembled.

  - E-mailed Gary Proctor a copy of the new drawing with filter numbers included.

  - Contacted Gray Proctor to arrange pickup of unit.

Bill Boisvert - Cell (919) 971-3910

Project Manager – avani environmental

E-mail bboisvert@avanienvironmental.com

CUST0MER REMARKS: _____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________