## Booths 1-7
Location # | Booth 1 Slot 1 |  |  | Location # | Booth 1 Slot 2 |  |  | Location # | Booth 1 Slot 4 |  |  | Location # | Booth 1 Slot 5 |  |  | Booth 1
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 301.3021
1 |  | 1080 | 333.75 | 1 |  | 1100 | 169.9653 | 1 |  | 710 | 219.4097 | 1 |  | 610 | 188.5069 | Slot 2 | 148.0758
2 |  | 925 | 285.8507 | 2 |  | 905 | 139.8351 | 2 |  | 700 | 216.3194 | 2 |  | 750 | 231.7708 | Slot 3 | 217.3495
3 |  | 920 | 284.3056 | 3 |  | 870 | 134.4271 | 3 |  | 700 | 216.3194 | 3 |  | 780 | 241.0417 | Slot 5 | 220.4398
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 975 | 301.3021 | Average |  | 958.3333 | 148.0758 | Average |  | 703.3333 | 217.3495 | Average |  | 713.3333 | 220.4398 | Total | 887.1672
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 2 Slot 1 |  |  | Location # | Booth 2 Slot 2 |  |  | Location # | Booth 2 Slot 4 |  |  | Location # | Booth 2 Slot 5 |  |  | Booth 2
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot1 | 305.9375
1 |  | 900 | 278.125 | 1 |  | 720 | 111.25 | 1 |  | 630 | 194.6875 | 1 |  | 730 | 225.5903 | Slot 2 | 124.1262
2 |  | 1030 | 318.2986 | 2 |  | 820 | 126.7014 | 2 |  | 670 | 207.0486 | 2 |  | 650 | 200.8681 | Slot 3 | 202.4132
3 |  | 1040 | 321.3889 | 3 |  | 870 | 134.4271 | 3 |  | 665 | 205.5035 | 3 |  | 630 | 194.6875 | Slot5 | 207.0486
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 990 | 305.9375 | Average |  | 803.3333 | 124.1262 | Average |  | 655 | 202.4132 | Average |  | 670 | 207.0486 | Total | 839.5255
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 3 Slot 1 |  |  | Location # | Booth 3 Slot 2 |  |  | Location # | Booth 3 Slot 4 |  |  | Location # | Booth 3 Slot 5 |  |  | Booth 3
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 232.2859
1 |  | 770 | 237.9514 | 1 |  | 650 | 100.434 | 1 |  | 505 | 156.059 | 1 |  | 550 | 169.9653 | Slot 2 | 92.9659
2 |  | 745 | 230.2257 | 2 |  | 575 | 88.8455 | 2 |  | 510 | 157.6042 | 2 |  | 485 | 149.8785 | Slot 3 | 156.059
3 |  | 740 | 228.6806 | 3 |  | 580 | 89.6181 | 3 |  | 500 | 154.5139 | 3 |  | 460 | 142.1528 | Slot 5 | 153.9988
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 751.6667 | 232.2859 | Average |  | 601.6667 | 92.9659 | Average |  | 505 | 156.059 | Average |  | 498.3333 | 153.9988 | Total | 635.3096
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 4 Slot 1 |  |  | Location # | Booth 4 Slot 2 |  |  | Location # | Booth 4 Slot 4 |  |  | Location # | Booth 4 Slot 5 |  |  | Booth 4
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 186.9618
1 |  | 560 | 173.0556 | 1 |  | 365 | 56.3976 | 1 |  | 415 | 128.2465 | 1 |  | 450 | 139.0625 | Slot 2 | 58.7153
2 |  | 655 | 202.4132 | 2 |  | 390 | 60.2604 | 2 |  | 365 | 112.7951 | 2 |  | 470 | 145.2431 | Slot 3 | 113.3102
3 |  | 600 | 185.4167 | 3 |  | 385 | 59.4878 | 3 |  | 320 | 98.8889 | 3 |  | 415 | 128.2465 | Slot 5 | 137.5174
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 605 | 186.9618 | Average |  | 380 | 58.7153 | Average |  | 366.6667 | 113.3102 | Average |  | 445 | 137.5174 | Total | 496.5046
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 5 Slot 1 |  |  | Location # | Booth 5 Slot 2 |  |  | Location # | Booth 5 Slot 4 |  |  | Location # | Booth 5 Slot 5 |  |  | Booth 5
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 139.5775
1 |  | 445 | 137.5174 | 1 |  | 260 | 40.1736 | 1 |  | 350 | 108.1597 | 1 |  | 410 | 126.7014 | Slot 2 | 39.9161
2 |  | 440 | 135.9722 | 2 |  | 265 | 40.9462 | 2 |  | 370 | 114.3403 | 2 |  | 400 | 123.6111 | Slot 3 | 105.5845
3 |  | 470 | 145.2431 | 3 |  | 250 | 38.6285 | 3 |  | 305 | 94.2535 | 3 |  | 385 | 118.9757 | Slot 5 | 123.0961
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 451.6667 | 139.5775 | Average |  | 258.3333 | 39.9161 | Average |  | 341.6667 | 105.5845 | Average |  | 398.3333 | 123.0961 | Total | 408.1742
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 6 Slot 1 |  |  | Location # | Booth 6 Slot 2 |  |  | Location # | Booth 6 Slot 4 |  |  | Location # | Booth 6 Slot 5 |  |  | Booth 6
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 248.2523
1 |  | 905 | 279.6701 | 1 |  | 630 | 97.3438 | 1 |  | 650 | 200.8681 | 1 |  | 610 | 188.5069 | Slot 2 | 88.588
2 |  | 800 | 247.2222 | 2 |  | 540 | 83.4375 | 2 |  | 560 | 173.0556 | 2 |  | 650 | 200.8681 | Slot 3 | 167.9051
3 |  | 705 | 217.8646 | 3 |  | 550 | 84.9826 | 3 |  | 420 | 129.7917 | 3 |  | 620 | 191.5972 | Slot 5 | 193.6574
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 803.3333 | 248.2523 | Average |  | 573.3333 | 88.588 | Average |  | 543.3333 | 167.9051 | Average |  | 626.6667 | 193.6574 | Total | 698.4028
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 7 Slot 1 |  |  | Location # | Booth 7 Slot 2 |  |  | Location # | Booth 7 Slot 4 |  |  | Location # | Booth 7 Slot 5 |  |  | Booth 7
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 251.8576
1 |  | 830 | 256.4931 | 1 |  | 550 | 84.9826 | 1 |  | 580 | 179.2361 | 1 |  | 600 | 185.4167 | Slot 2 | 90.1331
2 |  | 810 | 250.3125 | 2 |  | 610 | 94.2535 | 2 |  | 650 | 200.8681 | 2 |  | 590 | 182.3264 | Slot 3 | 175.1157
3 |  | 805 | 248.7674 | 3 |  | 590 | 91.1632 | 3 |  | 470 | 145.2431 | 3 |  | 560 | 173.0556 | Slot 5 | 180.2662
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 815 | 251.8576 | Average |  | 583.3333 | 90.1331 | Average |  | 566.6667 | 175.1157 | Average |  | 583.3333 | 180.2662 | Total | 697.3727
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0

## Booths 8-15
Location # | Booth 8 Slot 1 |  |  | Location # | Booth 8 Slot 2 |  |  | Location # | Booth 8 Slot 4 |  |  | Location # | Booth 8 Slot 5 |  |  | Booth 8
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 226.6204
1 |  | 705 | 217.8646 | 1 |  | 550 | 84.9826 | 1 |  | 405 | 125.1562 | 1 |  | 550 | 169.9653 | Slot 2 | 84.7251
2 |  | 750 | 231.7708 | 2 |  | 550 | 84.9826 | 2 |  | 425 | 131.3368 | 2 |  | 530 | 163.7847 | Slot 3 | 128.7616
3 |  | 745 | 230.2257 | 3 |  | 545 | 84.2101 | 3 |  | 420 | 129.7917 | 3 |  | 505 | 156.059 | Slot 5 | 163.2697
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 733.3333 | 226.6204 | Average |  | 548.3333 | 84.7251 | Average |  | 416.6667 | 128.7616 | Average |  | 528.3333 | 163.2697 | Total | 603.3767
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 9 Slot 1 |  |  | Location # | Booth 9 Slot 2 |  |  | Location # | Booth 9 Slot 4 |  |  | Location # | Booth 9 Slot 5 |  |  | Booth 9
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 193.6574
1 |  | 670 | 207.0486 | 1 |  | 445 | 68.7587 | 1 |  | 420 | 129.7917 | 1 |  | 430 | 132.8819 | Slot 2 | 67.2135
2 |  | 660 | 203.9583 | 2 |  | 440 | 67.9861 | 2 |  | 410 | 126.7014 | 2 |  | 415 | 128.2465 | Slot 3 | 124.6412
3 |  | 550 | 169.9653 | 3 |  | 420 | 64.8958 | 3 |  | 380 | 117.4306 | 3 |  | 405 | 125.1562 | Slot 5 | 128.7616
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 626.6667 | 193.6574 | Average |  | 435 | 67.2135 | Average |  | 403.3333 | 124.6412 | Average |  | 416.6667 | 128.7616 | Total | 514.2737
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 10 Slot 1 |  |  | Location # | Booth 10 Slot 2 |  |  | Location # | Booth 10 Slot 4 |  |  | Location # | Booth 10 Slot 5 |  |  | Booth 10
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 187.9919
1 |  | 650 | 200.8681 | 1 |  | 370 | 57.1701 | 1 |  | 405 | 125.1562 | 1 |  | 340 | 105.0694 | Slot 2 | 65.9259
2 |  | 580 | 179.2361 | 2 |  | 460 | 71.0764 | 2 |  | 420 | 129.7917 | 2 |  | 340 | 105.0694 | Slot 3 | 120.0058
3 |  | 595 | 183.8715 | 3 |  | 450 | 69.5312 | 3 |  | 340 | 105.0694 | 3 |  | 300 | 92.7083 | Slot 5 | 100.9491
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 608.3333 | 187.9919 | Average |  | 426.6667 | 65.9259 | Average |  | 388.3333 | 120.0058 | Average |  | 326.6667 | 100.9491 | Total | 474.8727
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 11 Slot 1 |  |  | Location # | Booth 11 Slot 2 |  |  | Location # | Booth 11 Slot 4 |  |  | Location # | Booth 11 Slot 5 |  |  | Booth 11
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 275.0347
1 |  | 845 | 261.1285 | 1 |  | 560 | 86.5278 | 1 |  | 660 | 203.9583 | 1 |  | 545 | 168.4201 | Slot 2 | 96.3137
2 |  | 900 | 278.125 | 2 |  | 630 | 97.3438 | 2 |  | 670 | 207.0486 | 2 |  | 620 | 191.5972 | Slot 3 | 200.8681
3 |  | 925 | 285.8507 | 3 |  | 680 | 105.0694 | 3 |  | 620 | 191.5972 | 3 |  | 510 | 157.6042 | Slot 5 | 172.5405
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 890 | 275.0347 | Average |  | 623.3333 | 96.3137 | Average |  | 650 | 200.8681 | Average |  | 558.3333 | 172.5405 | Total | 744.7569
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 12 Slot 1 |  |  | Location # | Booth 12 Slot 2 |  |  | Location # | Booth 12 Slot 4 |  |  | Location # | Booth 12 Slot 5 |  |  | Booth 12
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 262.1586
1 |  | 835 | 258.0382 | 1 |  | 470 | 72.6215 | 1 |  | 565 | 174.6007 | 1 |  | 550 | 169.9653 | Slot 2 | 80.0897
2 |  | 905 | 279.6701 | 2 |  | 535 | 82.6649 | 2 |  | 520 | 160.6944 | 2 |  | 570 | 176.1458 | Slot 3 | 160.1794
3 |  | 805 | 248.7674 | 3 |  | 550 | 84.9826 | 3 |  | 470 | 145.2431 | 3 |  | 630 | 194.6875 | Slot 5 | 180.2662
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 848.3333 | 262.1586 | Average |  | 518.3333 | 80.0897 | Average |  | 518.3333 | 160.1794 | Average |  | 583.3333 | 180.2662 | Total | 682.6939
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 13 Slot 1 |  |  | Location # | Booth 13 Slot 2 |  |  | Location # | Booth 13 Slot 4 |  |  | Location # | Booth 13 Slot 5 |  |  | Booth 13
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 227.6505
1 |  | 720 | 222.5 | 1 |  | 450 | 69.5312 | 1 |  | 410 | 126.7014 | 1 |  | 490 | 151.4236 | Slot 2 | 76.2269
2 |  | 770 | 237.9514 | 2 |  | 500 | 77.2569 | 2 |  | 380 | 117.4306 | 2 |  | 510 | 157.6042 | Slot 3 | 122.581
3 |  | 720 | 222.5 | 3 |  | 530 | 81.8924 | 3 |  | 400 | 123.6111 | 3 |  | 490 | 151.4236 | Slot 5 | 153.4838
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 736.6667 | 227.6505 | Average |  | 493.3333 | 76.2269 | Average |  | 396.6667 | 122.581 | Average |  | 496.6667 | 153.4838 | Total | 579.9421
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 14 Slot 1 |  |  | Location # | Booth 14 Slot 2 |  |  | Location # | Booth 14 Slot 4 |  |  | Location # | Booth 14 Slot 5 |  |  | Booth 14
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 199.838
1 |  | 625 | 193.1424 | 1 |  | 450 | 69.5312 | 1 |  | 430 | 132.8819 | 1 |  | 450 | 139.0625 | Slot 2 | 72.364
2 |  | 640 | 197.7778 | 2 |  | 450 | 69.5312 | 2 |  | 500 | 154.5139 | 2 |  | 420 | 129.7917 | Slot 3 | 137.5174
3 |  | 675 | 208.5938 | 3 |  | 505 | 78.0295 | 3 |  | 405 | 125.1562 | 3 |  | 430 | 132.8819 | Slot 5 | 133.912
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 646.6667 | 199.838 | Average |  | 468.3333 | 72.364 | Average |  | 445 | 137.5174 | Average |  | 433.3333 | 133.912 | Total | 543.6314
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # | Booth 15 Slot 1 |  |  | Location # | Booth 15 Slot 2 |  |  | Location # | Booth 15 Slot 4 |  |  | Location # | Booth 15 Slot 5 |  |  | Booth 15
Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Test Point |  | V | CFM | Slot 1 | 189.537
1 |  | 700 | 216.3194 | 1 |  | 485 | 74.9392 | 1 |  | 445 | 137.5174 | 1 |  | 480 | 148.3333 | Slot 2 | 75.1968
2 |  | 560 | 173.0556 | 2 |  | 490 | 75.7118 | 2 |  | 440 | 135.9722 | 2 |  | 470 | 145.2431 | Slot 3 | 127.7315
3 |  | 580 | 179.2361 | 3 |  | 485 | 74.9392 | 3 |  | 355 | 109.7049 | 3 |  | 480 | 148.3333 | Slot 5 | 147.3032
4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0 | 4 |  |  | 0
Average |  | 613.3333 | 189.537 | Average |  | 486.6667 | 75.1968 | Average |  | 413.3333 | 127.7315 | Average |  | 476.6667 | 147.3032 | Total | 539.7685
Duct Area: | 0.30903 |  |  | Duct Area: | 0.15451 |  |  | Duct Area: | 0.30903 |  |  | Duct Area: | 0.30903
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
1 | 44.5 | 0.30903 |  | 0.5 | 44.5 | 0.15451 |  | 1 | 44.5 | 0.30903 |  | 1 | 44.5 | 0.30903
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0

## System Totals
Booth 1 |  | Booth 2 |  | Booth 3 |  | Booth 4 |  | Booth 5
Slot 1 | 301.3021 | Slot1 | 305.9375 | Slot 1 | 232.2859 | Slot 1 | 186.9618 | Slot 1 | 139.5775
Slot 2 | 148.0758 | Slot 2 | 124.1262 | Slot 2 | 92.9659 | Slot 2 | 58.7153 | Slot 2 | 39.9161
Slot 3 | 217.3495 | Slot 3 | 202.4132 | Slot 3 | 156.059 | Slot 3 | 113.3102 | Slot 3 | 105.5845
Slot 5 | 220.4398 | Slot5 | 207.0486 | Slot 5 | 153.9988 | Slot 5 | 137.5174 | Slot 5 | 123.0961
Total | 887.1672 | Total | 839.5255 | Total | 635.3096 | Total | 496.5046 | Total | 408.1742
Booth 6 |  | Booth 7 |  | Booth 8 |  | Booth 9 |  | Booth 10
Slot 1 | 248.2523 | Slot 1 | 251.8576 | Slot 1 | 226.6204 | Slot 1 | 193.6574 | Slot 1 | 187.9919
Slot 2 | 88.588 | Slot 2 | 90.1331 | Slot 2 | 84.7251 | Slot 2 | 67.2135 | Slot 2 | 65.9259
Slot 3 | 167.9051 | Slot 3 | 175.1157 | Slot 3 | 128.7616 | Slot 3 | 124.6412 | Slot 3 | 120.0058
Slot 5 | 193.6574 | Slot 5 | 180.2662 | Slot 5 | 163.2697 | Slot 5 | 128.7616 | Slot 5 | 100.9491
Total | 698.4028 | Total | 697.3727 | Total | 603.3767 | Total | 514.2737 | Total | 474.8727
Booth 11 |  | Booth 12 |  | Booth 13 |  | Booth 14 |  | Booth 15
Slot 1 | 275.0347 | Slot 1 | 262.1586 | Slot 1 | 227.6505 | Slot 1 | 199.838 | Slot 1 | 189.537
Slot 2 | 96.3137 | Slot 2 | 80.0897 | Slot 2 | 76.2269 | Slot 2 | 72.364 | Slot 2 | 75.1968
Slot 3 | 200.8681 | Slot 3 | 160.1794 | Slot 3 | 122.581 | Slot 3 | 137.5174 | Slot 3 | 127.7315
Slot 5 | 172.5405 | Slot 5 | 180.2662 | Slot 5 | 153.4838 | Slot 5 | 133.912 | Slot 5 | 147.3032
Total | 744.7569 | Total | 682.6939 | Total | 579.9421 | Total | 543.6314 | Total | 539.7685
System Total
|  |  |  | Booth 1 | 887.1672
|  |  |  | Booth 2 | 839.5255
|  |  |  | Booth 3 | 635.3096
|  |  |  | Booth 4 | 496.5046
|  |  |  | Booth 5 | 408.1742
|  |  |  | Booth 6 | 698.4028
|  |  |  | Booth 7 | 697.3727
|  |  |  | Booth 8 | 603.3767
|  |  |  | Booth 9 | 514.2737
|  |  |  | Booth 10 | 474.8727
|  |  |  | Booth 11 | 744.7569
|  |  |  | Booth 12 | 682.6939
|  |  |  | Booth 13 | 579.9421
|  |  |  | Booth 14 | 543.6314
|  |  |  | Booth 15 | 539.7685
|  |  |  | Total | 9345.7726