Customer:	 Eaton Corp.

221 Heywood Road

Arden, NC 28704

Contact:	 Steve Kraus

Phone: 	828-808-7141

Email:		SteveKraus@Eaton.com

Date:  11/29/12

Project #:  Case #1187

Sales Order #:

Serial #:

Model #:

AEI Crew:   Bill Boisvert

SCOPE OF PROJECT:        Installation – Service – (Warranty) – Demo – Delivery – Engineering

- Removed all fan transition, 34” 90degree elbow and 34” to 20” reducer.

- Re-install motor onto the fan base.

- Eaton tech rewired the motor

- Checked voltage at inlet to the motor starter – Sat.

- Energized the motor started and checked voltage at outlet (to motor) – Sat.

- Checked voltage at inlet to the service disconnect – Sat.

- Started motor – ran fine – 10.5 amps.

- Installed fan wheel and ran fan – Sat. – approx. 17 amps.

- Installed fan inlet nozzle and ran fan – Sat. - approx.. 30 amps

- Re-installed fan transition,  34” to 20” reducer and 20” 90

- Installed remaining 20” duct work.

- Ran fan for approximately 30 minutes with no problem.

- Collector is running at 1.9 to 2 inch H2O – system is clean.

- Pulse system did not pulse at shut down.  Will contact manufacturer for help in resolving pulse issue.

Please review, sign and e-mail a copy back to me.

Thanks,

Bill Boisvert

Bill Boisvert - Cell (919) 971-3910

Project Manager – Avani Environmental Intl.

E-mail bboisvert@avanienvironmental.com

CUST0MER REMARKS: __________________________________________________________________________________________________________________________________________________________________ _________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________