Date: 06/27/08		     Project#: Absolent Service 	IAQ Crew:  Bill Boisvert

Customer:	Eaton Automotive				Installation:

2564 Durham Road				Service:  X

Roxboro, NC 27573				Warranty:

Attention: Mike Riley				Repair:

# Scope Of Project

- ODR-9000 - SN:??? (Cold Formers)

  - Found HEPA gauge on tower two bad, gauge replaced

  - Pump box is leaking. Found pump discharge piping placing box under undo pressure.  Removed section of pipe and replace with high pressure flex tubing.

    - If leak continues will have to have unit pumped out, Pump box removed and resealed.

  - Filter gauge readings as follows:

    - Tower 1

      - 1st Stage – 400PA

      - 2nd Stage – 400PA

      - HEPA – 300PA

    - Tower 2

      - 1st Stage – 600PA

      - 2nd Stage – 400PA

      - HEPA – 200PA

    - Tower 3

      - 1st Stage – 500PA

      - 2nd Stage – 400PA

      - HEPA – 200PA

- ODR-3000 – SN: 20020643 (Cold Former)

  - First stage gauge bad

  - Unit needs oil add to plenum for spray system

  - Filter gauge readings as follows:

    - N /A

    - 2nd Stage – 400PA

    - HEPA – 400PA

- ODR-3000 - SN: 20041094 (Cold Former)

  - Found motor bad

  - Found pump and fan wired to run backward

  - Replaced motor.

  - Rewired unit so that fan and pump run in correct rotation.

  - Found union on pump loose, union tightened.

  - Filter gauge readings as follows:

    - 1st Stage – Bad

    - 2nd Stage – Bad

    - HEPA – 400PA

- ODR-3000 – SN: 20020798 (Cold Former)

  - Inspected union for possible low airflow.

    - Found 1st Stage filter not tightly in place.

    - Filter dropped on both sides; ensured filter was in place, filter then retightened.

    - Measured airflow at 12” inlet and found correct velocity, 2600 fpm.

  - Filter gauge readings as follows:

    - 1st Stage – Bad

    - 2nd Stage – 300

    - HEPA – 200PA

- ODR-3000 – SN: 20001676 (Hydromats) (Freq. Drive)

  - Found running backwards – Corrected

  - Filter gauge readings as follows:

    - 1st Stage – 100PA

    - 2nd Stage – 100PA

    - HEPA – 100PA

- ODR-3000 – SN: 20001646 (Hydromats)

  - Unit OK

  - Filter gauge readings as follows:

    - 1st Stage – 400PA

    - 2nd Stage – 200PA

    - HEPA – 200PA

- ODR-9000 – SN: ??? (Hydromats)

  - Did not have lift to get to unit

  - Filter gauges appeared to all be OK, HEPA gauges highest at about 800PA.

- ODR-3000 – SN: 20070818 (Cold Former)

  - Unit needs oil add to plenum for spray system

  - Filter gauge readings as follows:

    - 1st Stage – 200PA

    - 2nd Stage – 100PA

    - HEPA – 100PA

- ODR-9000 – SN: 20030167

  - Unit OK

  - Filter gauge readings as follows:

    - Tower 1

      - 1st Stage – 100PA

      - 2nd Stage – 200PA

      - HEPA – 50PA

    - Tower 2

      - 1st Stage – 200PA

      - 2nd Stage – 100PA

      - HEPA – 100PA

    - Tower 3

      - 1st Stage – 200PA

      - 2nd Stage –200PA

      - HEPA – 100PA

- ODR-9000 – SN: 20001393 (First Unit installed)

  - Unit OK

  - One bad gauge (Tower 3 – HEPA)

  - Filter gauge readings as follows:

    - Tower 1

      - 1st Stage – 400PA

      - 2nd Stage – 400PA

      - HEPA – 300PA

    - Tower 2

      - 1st Stage – 600PA

      - 2nd Stage – 400PA

      - HEPA – 200PA

    - Tower 3

      - 1st Stage – 500PA

      - 2nd Stage – 400PA

      - HEPA – 200PA

- ODR-9000 – SN: 20040159 (ID Grinders)

  - Unit OK

  - Filter gauge readings as follows:

    - Tower 1

      - 1st Stage – 300PA

      - 2nd Stage – 200PA

      - HEPA – 500PA

    - Tower 2

      - 1st Stage – 600PA

      - 2nd Stage – 200PA

      - HEPA – 200PA

    - Tower 3

      - 1st Stage – 600PA

      - 2nd Stage – 200PA

      - HEPA – 250PA

- ODR-2000 – SN: 20040090 (two OD Grinders)

  - Found one section of 6” missing

  - Unit OK

  - Filter gauge readings as follows:

    - 1st Stage – 400PA

    - HEPA – <100PA

- ODR-3000 – SN: 20010799 (Asset #3091) (AFM)

  - Unit OK

  - Filter gauge readings as follows:

    - 1st Stage – 200

    - 2nd Stage – 200

    - HEPA – 400PA

- ODR-3000 – SN: 20001145 (Asset #3071) (AFM)

  - Unit OK

  - Filter gauge readings as follows:

    - 1st Stage – 100

    - 2nd Stage – 200

    - HEPA – 400PA

- ODR-3000 – SN: 20030758 (Asset #3768) (AFM)

  - Unit OK

  - Filter gauge readings as follows:

    - 1st Stage – 200

    - 2nd Stage – 300

    - HEPA – 100PA

CUSTOMER REMARKS:

CUSTOMER SIGNATURE:						DATE:

TITLE OR DEPARTMENT: