Customer:	Hennessy Industries Inc.

1601 JP Hennessy Dr.
		La Vergne, TN 37086

Contact: Doug Lentz

Phone:  615-641-7533 X7623

Email:

Date:  4/27/11

Project #:

Sales Order #:

Serial #: 102007

Model #: SDC-25-15

OE Crew:  Bill Boisvert

SCOPE OF PROJECT:        Installation – Service – (Warranty) – Demo – Delivery - Engineering

When I arrived on site I found that the unit in question started with no problem.  When I stop the fans and restarted the 15 hp overload relay tripped.  I let in rest and the unit restarted once.  I replaced the overload relay with one that I had on my truck and the unit started.  I stopped and restarted the unit five times in a short period and unit preformed with no trips.  I then let the unit run for twenty minutes and repeated the start/stop test with no trips.  The overload trip device was one that I got from our stock and did not match the ones that came with these units.

Unit appears to be operating correctly.  Sorry for any inconvenience.

Thanks,

Bill Boisvert - Cell (919) 971-3910

Project Manager – avani environmental

E-mail bboisvert@avanienvironmental.com

CUST0MER REMARKS: _____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________