## Sheet1
FIRETRACE
| HFC 227ea FM-200 or FE-227 | FE-25 | ABC Dry Chemical | FK-5-1-12 NOVEC 1230 | CO2
System Type | INDIRECT | DIRECT | INDIRECT | INDIRECT | INDIRECT
Approval Type | UL and FM | FM | UL and FM | UL and FM | UL and FM
Types of Fire | Class A, B and C fires in occupied spaces. | Class A, B and C fires in occupied spaces. | Class A, B and C fires. | Typically Class B and C fires. | Typically Class B fires.
Sizing Guidelines* | 12# - 300 ft3 6# - 150 ft3 3# - 75 ft3 1# - 25 ft3 | 12# - 350 ft3 6# - 175 ft3 3# - 85 ft3 | 20# - 1500 ft3 10# - 750 ft3 5# - 375 ft3 2.5# - 175 ft3 | 10# - 180 ft3 5# - 90 ft3 2.5# - 45 ft3 | 50# - 725 ft3 35# - 555 ft3 20# - 300 ft3 10# - 140 ft3 5# - 70 ft3
Pressure | Low | Mid | Low | Low | High
People Safe** | Yes | Yes | Yes | Yes | NO
List Price | $ / lb | $ / lb | $/ lb | $/ lb | $/ lb
Limitiations/ Considerations | A versatile clean agent, however for applications where temperatures may fall below freezing it may not flow properly | Very cost effective, usually requires 20% less agent per ft3 than HFC-227ea | Thorough clean-up required and mildly corrosive if moisture is present. | Completely non-conductive, non-corrosive agent requires no cleanup and is a liquid at room temperature. Extremely low global warming potential. | Very cold discharge can cause thermal shock damage to electronics
Notes:
*Protected volume values should only be used as a starting point for system type and size determination
*Does not take into consideration the protectable volume reduction due to air flow or uncloseable openings
*Agent requirements for said volume need to also consider the lowest ambient air temperature expected
*Agent effectiveness is dependent on boiling point of agent and ambient air conditions (ie. Altitude)
** When using design concentrations