## Block #1
Block Line #1 CNC Cell #1
ODF-6000F SN:20071329
Gauge Readings - PA
Tower # | 1 | 2 | 3
1st Stage | 200 | 200 | 200
2nd Stage | 150 | 150 | 150
HEPA | 100 | 100 | 100
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.29 | 2156.7585 | 3009.8763 | 1 |  | 0 | 0 | 1 | 0.47 | 2745.6897 | 957.9406 | 1 | 0.39 | 2501.1217 | 872.6136
2 | 0.28 | 2119.2468 | 2957.5266 | 2 |  | 0 | 0 | 2 | 0.45 | 2686.6357 | 937.3373 | 2 | 0.45 | 2686.6357 | 937.3373
3 | 0.31 | 2229.8896 | 3111.9349 | 3 |  | 0 | 0 | 3 | 0.43 | 2626.2541 | 916.2709 | 3 | 0.38 | 2468.8478 | 861.3536
4 | 0.26 | 2042.1573 | 2849.944 | 4 |  | 0 | 0 | 4 | 0.45 | 2686.6357 | 937.3373 | 4 | 0.43 | 2626.2541 | 916.2709
5 | 0.29 | 2156.7585 | 3009.8763 | 5 |  | 0 | 0 | 5 | 0.32 | 2265.5701 | 790.4322 | 5 | 0.42 | 2595.5366 | 905.5539
6 | 0.28 | 2119.2468 | 2957.5266 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.285 | 2138.0849 | 2983.8163 | Average | 0 | 3950 | 1378.1111 | Average | 0.424 | 2607.8671 | 909.8558 | Average | 0.414 | 2576.9304 | 899.0624
Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.3 | 2193.6288 | 3061.3309 | 1 |  | 0 | 0 | 1 | 0.59 | 3076.2989 | 1073.2865 | 1 | 0.58 | 3050.1171 | 1064.152
2 | 0.29 | 2156.7585 | 3009.8763 | 2 |  | 0 | 0 | 2 | 0.58 | 3050.1171 | 1064.152 | 2 | 0.59 | 3076.2989 | 1073.2865
3 | 0.34 | 2335.2962 | 3259.0356 | 3 |  | 0 | 0 | 3 | 0.61 | 3128.005 | 1091.3262 | 3 | 0.63 | 3178.8702 | 1109.0725
4 | 0.32 | 2265.5701 | 3161.729 | 4 |  | 0 | 0 | 4 | 0.6 | 3102.2597 | 1082.3439 | 4 | 0.64 | 3204 | 1117.84
5 | 0.32 | 2265.5701 | 3161.729 | 5 |  | 0 | 0 | 5 | 0.57 | 3023.7087 | 1054.9384 | 5 | 0.55 | 2970.1875 | 1036.2654
6 | 0.3 | 2193.6288 | 3061.3309 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.31167 | 2235.8759 | 3120.2891 | Average | 0 | 2540 | 886.1778 | Average | 0.59 | 3076.2989 | 1073.2865 | Average | 0.598 | 3097.0849 | 1080.5385
Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Block #2
Block Line #2 CNC Cell #2
ODF-6000F SN:20071321
Gauge Readings - PA
Tower # | 1 | 2 | 3
1st Stage | 300 | 400 | 300
2nd Stage | 200 | 200 | 200
HEPA | 200 | 200 | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4 |  |  | Location # | TP5
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.45 | 2686.6357 | 3749.3493 | 1 | 0.55 | 2970.1875 | 1036.2654 | 1 | 0.55 | 2970.1875 | 1036.2654 | 1 | 0.56 | 2997.0676 | 1045.6436 | 1 |  | 0 | 0
2 | 0.44 | 2656.6165 | 3707.4559 | 2 | 0.56 | 2997.0676 | 1045.6436 | 2 | 0.58 | 3050.1171 | 1064.152 | 2 | 0.55 | 2970.1875 | 1036.2654 | 2 |  | 0 | 0
3 | 0.46 | 2716.3232 | 3790.7799 | 3 | 0.54 | 2943.0619 | 1026.8016 | 3 | 0.56 | 2997.0676 | 1045.6436 | 3 | 0.49 | 2803.5 | 978.11 | 3 |  | 0 | 0
4 | 0.41 | 2564.4513 | 3578.8342 | 4 | 0.53 | 2915.684 | 1017.2498 | 4 | 0.48 | 2774.7454 | 968.0778 | 4 | 0.48 | 2774.7454 | 968.0778 | 4 |  | 0 | 0
5 | 0.46 | 2716.3232 | 3790.7799 | 5 | 0.57 | 3023.7087 | 1054.9384 | 5 | 0.5 | 2831.9627 | 988.0403 | 5 | 0.5 | 2831.9627 | 988.0403 | 5 |  | 0 | 0
6 | 0.44 | 2656.6165 | 3707.4559 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.44333 | 2666.6604 | 3721.4728 | Average | 0.55 | 2970.1875 | 1036.2654 | Average | 0.534 | 2926.6659 | 1021.0812 | Average | 0.516 | 2876.9173 | 1003.7245 | Average | 0 | 3450 | 1203.6667
Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4 |  |  | Location # | TP5
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.47 | 2745.6897 | 3831.7625 | 1 | 0.55 | 2970.1875 | 1036.2654 | 1 | 0.55 | 2970.1875 | 1036.2654 | 1 | 0.56 | 2997.0676 | 1045.6436 | 1 |  | 0 | 0
2 | 0.45 | 2686.6357 | 3749.3493 | 2 | 0.56 | 2997.0676 | 1045.6436 | 2 | 0.58 | 3050.1171 | 1064.152 | 2 | 0.55 | 2970.1875 | 1036.2654 | 2 |  | 0 | 0
3 | 0.49 | 2803.5 | 3912.44 | 3 | 0.54 | 2943.0619 | 1026.8016 | 3 | 0.56 | 2997.0676 | 1045.6436 | 3 | 0.49 | 2803.5 | 978.11 | 3 |  | 0 | 0
4 | 0.5 | 2831.9627 | 3952.1612 | 4 | 0.53 | 2915.684 | 1017.2498 | 4 | 0.48 | 2774.7454 | 968.0778 | 4 | 0.48 | 2774.7454 | 968.0778 | 4 |  | 0 | 0
5 | 0.51 | 2860.1421 | 3991.4872 | 5 | 0.57 | 3023.7087 | 1054.9384 | 5 | 0.5 | 2831.9627 | 988.0403 | 5 | 0.5 | 2831.9627 | 988.0403 | 5 |  | 0 | 0
6 | 0.45 | 2686.6357 | 3749.3493 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.47833 | 2769.9239 | 3865.5827 | Average | 0.55 | 2970.1875 | 1036.2654 | Average | 0.534 | 2926.6659 | 1021.0812 | Average | 0.516 | 2876.9173 | 1003.7245 | Average | 0 | 3450 | 1203.6667
Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Block #3
Block Line #3 CNC Cell #3
ODF-6000F SN:20071330
Gauge Readings - PA
Tower # | 1 | 2 | 3
1st Stage | 200 | 200 | 200
2nd Stage | 200 | 100 | 100
HEPA | 100 | 100 | 100
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.35 | 2369.39 | 3306.6153 | 1 | 0.32 | 2265.5701 | 790.4322 | 1 | 0.22 | 1878.5115 | 655.3918 | 1 |  | 0 | 0
2 | 0.32 | 2265.5701 | 3161.729 | 2 | 0.36 | 2403 | 838.38 | 2 | 0.25 | 2002.5 | 698.65 | 2 |  | 0 | 0
3 | 0.25 | 2002.5 | 2794.6 | 3 | 0.34 | 2335.2962 | 814.7589 | 3 | 0.27 | 2081.059 | 726.0584 | 3 |  | 0 | 0
4 | 0.26 | 2042.1573 | 2849.944 | 4 | 0.35 | 2369.39 | 826.6538 | 4 | 0.26 | 2042.1573 | 712.486 | 4 |  | 0 | 0
5 | 0.31 | 2229.8896 | 3111.9349 | 5 | 0.36 | 2403 | 838.38 | 5 | 0.26 | 2042.1573 | 712.486 | 5 |  | 0 | 0
6 | 0.37 | 2436.1464 | 3399.7776 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.31 | 2229.8896 | 3111.9349 | Average | 0.346 | 2355.8117 | 821.9165 | Average | 0.252 | 2010.494 | 701.439 | Average | 0 | 5530 | 1929.3556
Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.3 | 2193.6288 | 3061.3309 | 1 | 0.52 | 2888.0466 | 1007.6074 | 1 | 0.53 | 2915.684 | 1017.2498 | 1 |  | 0 | 0
2 | 0.31 | 2229.8896 | 3111.9349 | 2 | 0.56 | 2997.0676 | 1045.6436 | 2 | 0.57 | 3023.7087 | 1054.9384 | 2 |  | 0 | 0
3 | 0.29 | 2156.7585 | 3009.8763 | 3 | 0.57 | 3023.7087 | 1054.9384 | 3 | 0.56 | 2997.0676 | 1045.6436 | 3 |  | 0 | 0
4 | 0.33 | 2300.6973 | 3210.751 | 4 | 0.54 | 2943.0619 | 1026.8016 | 4 | 0.54 | 2943.0619 | 1026.8016 | 4 |  | 0 | 0
5 | 0.34 | 2335.2962 | 3259.0356 | 5 | 0.54 | 2943.0619 | 1026.8016 | 5 | 0.59 | 3076.2989 | 1073.2865 | 5 |  | 0 | 0
6 | 0.35 | 2369.39 | 3306.6153 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.32 | 2265.5701 | 3161.729 | Average | 0.546 | 2959.3671 | 1032.4903 | Average | 0.558 | 2991.7109 | 1043.7747 | Average | 0 | 3420 | 1193.2
Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Block #4
Block Line #4 - Coolant System #1
ODF-4000TF SN:20071339
Gauge Readings - PA
1st Stage | 500
2nd Stage | 200
HEPA | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.61 | 3128.005 | 2455.4839 | 1 | 0.63 | 3178.8702 | 1109.0725 | 1 | 0.7 | 3350.8234 | 1169.0651
2 | 0.7 | 3350.8234 | 2630.3964 | 2 | 0.67 | 3278.2338 | 1143.7393 | 2 | 0.68 | 3302.6076 | 1152.2431
3 | 0.7 | 3350.8234 | 2630.3964 | 3 | 0.65 | 3228.9342 | 1126.5393 | 3 | 0.68 | 3302.6076 | 1152.2431
4 | 0.69 | 3326.8029 | 2611.5402 | 4 | 0.69 | 3326.8029 | 1160.6846 | 4 | 0.67 | 3278.2338 | 1143.7393
5 | 0.65 | 3228.9342 | 2534.7134 | 5 | 0.7 | 3350.8234 | 1169.0651 | 5 | 0.7 | 3350.8234 | 1169.0651
6 | 0.66 | 3253.6774 | 2554.1367 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.66833 | 3274.1538 | 2570.2108 | Average | 0.668 | 3273.3372 | 1142.031 | Average | 0.686 | 3317.1459 | 1157.3154
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.61 | 3128.005 | 2455.4839 | 1 | 0.63 | 3178.8702 | 1109.0725 | 1 | 0.7 | 3350.8234 | 1169.0651
2 | 0.7 | 3350.8234 | 2630.3964 | 2 | 0.67 | 3278.2338 | 1143.7393 | 2 | 0.68 | 3302.6076 | 1152.2431
3 | 0.7 | 3350.8234 | 2630.3964 | 3 | 0.65 | 3228.9342 | 1126.5393 | 3 | 0.68 | 3302.6076 | 1152.2431
4 | 0.69 | 3326.8029 | 2611.5402 | 4 | 0.69 | 3326.8029 | 1160.6846 | 4 | 0.67 | 3278.2338 | 1143.7393
5 | 0.65 | 3228.9342 | 2534.7134 | 5 | 0.7 | 3350.8234 | 1169.0651 | 5 | 0.7 | 3350.8234 | 1169.0651
6 | 0.66 | 3253.6774 | 2554.1367 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.66833 | 3274.1538 | 2570.2108 | Average | 0.668 | 3273.3372 | 1142.031 | Average | 0.686 | 3317.1459 | 1157.3154
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Block #6
Block Line #6 - Coolant System #3
ODF-4000TF SN:20071337
Gauge Readings - PA
1st Stage | 300
2nd Stage | 200
HEPA | 200
As Found |  |  |  | As Left
Location # | TP1 |  |  | Location # | TP1
Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 1.07 | 4142.8042 | 3252.1013 | 1 | 1.07 | 4142.8042 | 3252.1013
2 | 0.78 | 3537.1202 | 2776.6394 | 2 | 0.78 | 3537.1202 | 2776.6394
3 | 0.71 | 3374.673 | 2649.1183 | 3 | 0.71 | 3374.673 | 2649.1183
4 | 0.66 | 3253.6774 | 2554.1367 | 4 | 0.66 | 3253.6774 | 2554.1367
5 | 0.5 | 2831.9627 | 2223.0907 | 5 | 0.5 | 2831.9627 | 2223.0907
6 | 0.51 | 2860.1421 | 2245.2115 | 6 | 0.51 | 2860.1421 | 2245.2115
7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.705 | 3362.7693 | 2639.7739 | Average | 0.705 | 3362.7693 | 2639.7739
Duct Area: | 0.785 |  |  | Duct Area: | 0.785
Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 12 | 0.785

## Block #7
Block Line #7 - Intermediate Washer
ODF-6000F SN:20071322 |  |  |  | ODF-4000TF SN:20071333
Gauge Readings - PA
Tower # | 1 | 2 | 3 | Gauge Readings - PA
1st Stage | 100 | 100 | 100 | 1st Stage | 300
2nd Stage | 100 | 100 | 100 | 2nd Stage | 200
HEPA | 100 | 100 | 100 | HEPA | 100
As Found
Location # | TP1A |  |  | Location # | TP1B |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.37 | 2436.1464 | 3399.7776 | 1 | 0.56 | 2997.0676 | 2352.698 | 1 | 0.17 | 1651.3038 | 324.0684 | 1 | 2.9 | 6820.2692 | 3717.994 | 1 | 0.1 | 1266.4922 | 690.4142
2 | 0.32 | 2265.5701 | 3161.729 | 2 | 0.54 | 2943.0619 | 2310.3036 | 2 | 0.15 | 1551.1298 | 304.4092 | 2 | 3.14 | 7096.8781 | 3868.7842 | 2 | 0.08 | 1132.7851 | 617.5252
3 | 0.24 | 1962.0413 | 2738.1376 | 3 | 0.56 | 2997.0676 | 2352.698 | 3 | 0.13 | 1444.0233 | 283.3896 | 3 | 2.99 | 6925.2924 | 3775.2462 | 3 | 0.15 | 1551.1298 | 845.5812
4 | 0.32 | 2265.5701 | 3161.729 | 4 | 0.57 | 3023.7087 | 2373.6113 | 4 | 0.14 | 1498.5338 | 294.0873 | 4 | 3.15 | 7108.1699 | 3874.9398 | 4 | 0.09 | 1201.5 | 654.9844
5 | 0.39 | 2501.1217 | 3490.4543 | 5 | 0.53 | 2915.684 | 2288.8119 | 5 | 0.12 | 1387.3727 | 272.2719 | 5 | 3.2 | 7164.3618 | 3905.5722 | 5 | 0.14 | 1498.5338 | 816.909
6 | 0.4 | 2532.9844 | 3534.9205 | 6 | 0.52 | 2888.0466 | 2267.1166 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.34 | 2335.2962 | 3259.0356 | Average | 0.54667 | 2961.1732 | 2324.521 | Average | 0.142 | 1509.1996 | 296.1804 | Average | 3.076 | 7024.1809 | 3829.1542 | Average | 0.112 | 1340.3294 | 730.6657
Duct Area: | 1.3956 |  |  | Duct Area: | 0.785 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 12 | 0.785 |  |  | 6 | 0.19625 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514
As Left
Location # | TP1A |  |  | Location # | TP1B |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.37 | 2436.1464 | 3399.7776 | 1 | 0.56 | 2997.0676 | 2352.698 | 1 | 0.17 | 1651.3038 | 324.0684 | 1 | 2.9 | 6820.2692 | 3717.994 | 1 | 0.1 | 1266.4922 | 690.4142
2 | 0.32 | 2265.5701 | 3161.729 | 2 | 0.54 | 2943.0619 | 2310.3036 | 2 | 0.15 | 1551.1298 | 304.4092 | 2 | 3.14 | 7096.8781 | 3868.7842 | 2 | 0.08 | 1132.7851 | 617.5252
3 | 0.24 | 1962.0413 | 2738.1376 | 3 | 0.56 | 2997.0676 | 2352.698 | 3 | 0.13 | 1444.0233 | 283.3896 | 3 | 2.99 | 6925.2924 | 3775.2462 | 3 | 0.15 | 1551.1298 | 845.5812
4 | 0.32 | 2265.5701 | 3161.729 | 4 | 0.57 | 3023.7087 | 2373.6113 | 4 | 0.14 | 1498.5338 | 294.0873 | 4 | 3.15 | 7108.1699 | 3874.9398 | 4 | 0.09 | 1201.5 | 654.9844
5 | 0.39 | 2501.1217 | 3490.4543 | 5 | 0.53 | 2915.684 | 2288.8119 | 5 | 0.12 | 1387.3727 | 272.2719 | 5 | 3.2 | 7164.3618 | 3905.5722 | 5 | 0.14 | 1498.5338 | 816.909
6 | 0.4 | 2532.9844 | 3534.9205 | 6 | 0.52 | 2888.0466 | 2267.1166 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.34 | 2335.2962 | 3259.0356 | Average | 0.54667 | 2961.1732 | 2324.521 | Average | 0.142 | 1509.1996 | 296.1804 | Average | 3.076 | 7024.1809 | 3829.1542 | Average | 0.112 | 1340.3294 | 730.6657
Duct Area: | 1.3956 |  |  | Duct Area: | 0.785 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 12 | 0.785 |  |  | 6 | 0.19625 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514

## Block #8
Block Line #8 - FB Hone A-Side
ODF-8000TF SN:20071318
Gauge Readings - PA
Tower # | 1 | 2
1st Stage | 200 | 200
2nd Stage | 200 | 200
HEPA | 200 | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4 |  |  | Location # | TP5
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.82 | 3626.6817 | 5061.2359 | 1 | 0.59 | 3076.2989 | 1073.2865 | 1 | 0.78 | 3537.1202 | 1234.0619 | 1 | 0.57 | 3023.7087 | 1054.9384 | 1 |  | 0 | 0
2 | 0.78 | 3537.1202 | 4936.2478 | 2 | 0.57 | 3023.7087 | 1054.9384 | 2 | 0.69 | 3326.8029 | 1160.6846 | 2 | 0.58 | 3050.1171 | 1064.152 | 2 |  | 0 | 0
3 | 0.72 | 3398.3552 | 4742.5935 | 3 | 0.55 | 2970.1875 | 1036.2654 | 3 | 0.71 | 3374.673 | 1177.3859 | 3 | 0.61 | 3128.005 | 1091.3262 | 3 |  | 0 | 0
4 | 0.75 | 3468.4317 | 4840.3892 | 4 | 0.56 | 2997.0676 | 1045.6436 | 4 | 0.8 | 3582.1809 | 1249.7831 | 4 | 0.58 | 3050.1171 | 1064.152 | 4 |  | 0 | 0
5 | 0.79 | 3559.7219 | 4967.7896 | 5 | 0.58 | 3050.1171 | 1064.152 | 5 | 0.76 | 3491.4781 | 1218.1379 | 5 | 0.44 | 2656.6165 | 926.864 | 5 |  | 0 | 0
6 | 0.77 | 3514.3732 | 4904.5031 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.77167 | 3518.1746 | 4909.8081 | Average | 0.57 | 3023.7087 | 1054.9384 | Average | 0.748 | 3463.8041 | 1208.4828 | Average | 0.556 | 2986.3446 | 1041.9024 | Average | 0 | 5490 | 1915.4
Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4 |  |  | Location # | TP5
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.7 | 3350.8234 | 4676.2602 | 1 | 0.59 | 3076.2989 | 1073.2865 | 1 | 0.61 | 3128.005 | 1091.3262 | 1 | 0.56 | 2997.0676 | 1045.6436 | 1 |  | 0 | 0
2 | 0.71 | 3374.673 | 4709.5436 | 2 | 0.63 | 3178.8702 | 1109.0725 | 2 | 0.61 | 3128.005 | 1091.3262 | 2 | 0.54 | 2943.0619 | 1026.8016 | 2 |  | 0 | 0
3 | 0.79 | 3559.7219 | 4967.7896 | 3 | 0.66 | 3253.6774 | 1135.1719 | 3 | 0.6 | 3102.2597 | 1082.3439 | 3 | 0.61 | 3128.005 | 1091.3262 | 3 |  | 0 | 0
4 | 0.73 | 3421.8735 | 4775.4146 | 4 | 0.63 | 3178.8702 | 1109.0725 | 4 | 0.59 | 3076.2989 | 1073.2865 | 4 | 0.59 | 3076.2989 | 1073.2865 | 4 |  | 0 | 0
5 | 0.75 | 3468.4317 | 4840.3892 | 5 | 0.61 | 3128.005 | 1091.3262 | 5 | 0.59 | 3076.2989 | 1073.2865 | 5 | 0.56 | 2997.0676 | 1045.6436 | 5 |  | 0 | 0
6 | 0.77 | 3514.3732 | 4904.5031 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.74167 | 3449.1089 | 4813.423 | Average | 0.624 | 3163.6965 | 1103.7786 | Average | 0.6 | 3102.2597 | 1082.3439 | Average | 0.572 | 3029.0088 | 1056.7875 | Average | 0 | 2520 | 879.2
Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Block #10
Block Line #10 - Linebore Cell
ODF-4000TF SN:20071336
Gauge Readings - PA
1st Stage | 250
2nd Stage | 200
HEPA | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.69 | 3326.8029 | 2611.5402 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 | 0.78 | 3537.1202 | 944.8287
2 | 0.89 | 3778.3094 | 2965.9729 | 2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 | 0.77 | 3514.3732 | 938.7525
3 | 0.85 | 3692.4276 | 2898.5556 | 3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 | 0.75 | 3468.4317 | 926.4807
4 | 0.76 | 3491.4781 | 2740.8103 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 | 0.65 | 3228.9342 | 862.5066
5 | 0.76 | 3491.4781 | 2740.8103 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 | 0.69 | 3326.8029 | 888.6491
6 | 0.69 | 3326.8029 | 2611.5402 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.77333 | 3521.9719 | 2764.7479 | Average | 0 | 4950 | 1322.2344 | Average | 0 | 4700 | 1255.4549 | Average | 0.728 | 3417.1828 | 912.7912
Duct Area: | 0.785 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.7 | 3350.8234 | 2630.3964 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 | 0.59 | 3076.2989 | 821.735
2 | 0.74 | 3445.2313 | 2704.5065 | 2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 | 0.62 | 3153.5402 | 842.3675
3 | 0.69 | 3326.8029 | 2611.5402 | 3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 | 0.72 | 3398.3552 | 907.762
4 | 0.77 | 3514.3732 | 2758.783 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 | 0.69 | 3326.8029 | 888.6491
5 | 0.73 | 3421.8735 | 2686.1707 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 | 0.64 | 3204 | 855.8463
6 | 0.69 | 3326.8029 | 2611.5402 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.72 | 3398.3552 | 2667.7088 | Average | 0 | 3400 | 908.2014 | Average | 0 | 3250 | 868.1337 | Average | 0.652 | 3233.898 | 863.8325
Duct Area: | 0.785 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712

## Block #11
Block Line #11 - GA Final Mill
ODF-4000TF SN:20071319
Gauge Readings - PA
1st Stage | 300
2nd Stage | 200
HEPA | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.7 | 3350.8234 | 2630.3964 | 1 | 0.45 | 2686.6357 | 937.3373 | 1 |  | 0 | 0
2 | 0.72 | 3398.3552 | 2667.7088 | 2 | 0.43 | 2626.2541 | 916.2709 | 2 |  | 0 | 0
3 | 0.64 | 3204 | 2515.14 | 3 | 0.45 | 2686.6357 | 937.3373 | 3 |  | 0 | 0
4 | 0.68 | 3302.6076 | 2592.547 | 4 | 0.5 | 2831.9627 | 988.0403 | 4 |  | 0 | 0
5 | 0.7 | 3350.8234 | 2630.3964 | 5 | 0.49 | 2803.5 | 978.11 | 5 |  | 0 | 0
6 | 0.73 | 3421.8735 | 2686.1707 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.695 | 3338.8347 | 2620.9853 | Average | 0.464 | 2728.1077 | 951.8065 | Average | 0 | 6500 | 2267.7778
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.7 | 3350.8234 | 2630.3964 | 1 | 0.58 | 3050.1171 | 1064.152 | 1 |  | 0 | 0
2 | 0.67 | 3278.2338 | 2573.4135 | 2 | 0.54 | 2943.0619 | 1026.8016 | 2 |  | 0 | 0
3 | 0.65 | 3228.9342 | 2534.7134 | 3 | 0.54 | 2943.0619 | 1026.8016 | 3 |  | 0 | 0
4 | 0.64 | 3204 | 2515.14 | 4 | 0.57 | 3023.7087 | 1054.9384 | 4 |  | 0 | 0
5 | 0.65 | 3228.9342 | 2534.7134 | 5 | 0.52 | 2888.0466 | 1007.6074 | 5 |  | 0 | 0
6 | 0.63 | 3178.8702 | 2495.4131 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.65667 | 3245.4506 | 2547.6787 | Average | 0.55 | 2970.1875 | 1036.2654 | Average | 0 | 4560 | 1590.9333
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Block #12
Block Line #12 - Final Wash
ODF-6000F SN:20071328
Gauge Readings - PA
Tower # | 1 | 2 | 3
1st Stage | 250 | 250 | 250
2nd Stage | 200 | 200 | 200
HEPA | 200 | 200 | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.54 | 2943.0619 | 4107.2064 | 1 | 0.39 | 2501.1217 | 490.8451 | 1 | 0.98 | 3964.7477 | 2161.3382 | 1 | 0.57 | 3023.7087 | 1648.3412
2 | 0.53 | 2915.684 | 4068.999 | 2 | 0.43 | 2626.2541 | 515.4024 | 2 | 0.96 | 3924.0826 | 2139.17 | 2 | 0.56 | 2997.0676 | 1633.8181
3 | 0.51 | 2860.1421 | 3991.4872 | 3 | 0.43 | 2626.2541 | 515.4024 | 3 | 0.89 | 3778.3094 | 2059.7034 | 3 | 0.58 | 3050.1171 | 1662.7375
4 | 0.49 | 2803.5 | 3912.44 | 4 | 0.46 | 2716.3232 | 533.0784 | 4 | 0.95 | 3903.5911 | 2127.9993 | 4 | 0.49 | 2803.5 | 1528.2969
5 | 0.52 | 2888.0466 | 4030.4294 | 5 | 0.42 | 2595.5366 | 509.3741 | 5 | 0.89 | 3778.3094 | 2059.7034 | 5 | 0.53 | 2915.684 | 1589.4527
6 | 0.52 | 2888.0466 | 4030.4294 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.51833 | 2883.4146 | 4023.9652 | Average | 0.426 | 2614.0105 | 512.9996 | Average | 0.934 | 3870.5792 | 2110.0032 | Average | 0.546 | 2959.3671 | 1613.2661
Duct Area: | 1.3956 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 6 | 0.19625 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.54 | 2943.0619 | 4107.2064 | 1 | 0.39 | 2501.1217 | 490.8451 | 1 | 0.98 | 3964.7477 | 2161.3382 | 1 | 0.57 | 3023.7087 | 1648.3412
2 | 0.53 | 2915.684 | 4068.999 | 2 | 0.43 | 2626.2541 | 515.4024 | 2 | 0.96 | 3924.0826 | 2139.17 | 2 | 0.56 | 2997.0676 | 1633.8181
3 | 0.51 | 2860.1421 | 3991.4872 | 3 | 0.43 | 2626.2541 | 515.4024 | 3 | 0.89 | 3778.3094 | 2059.7034 | 3 | 0.58 | 3050.1171 | 1662.7375
4 | 0.49 | 2803.5 | 3912.44 | 4 | 0.46 | 2716.3232 | 533.0784 | 4 | 0.95 | 3903.5911 | 2127.9993 | 4 | 0.49 | 2803.5 | 1528.2969
5 | 0.52 | 2888.0466 | 4030.4294 | 5 | 0.42 | 2595.5366 | 509.3741 | 5 | 0.89 | 3778.3094 | 2059.7034 | 5 | 0.53 | 2915.684 | 1589.4527
6 | 0.52 | 2888.0466 | 4030.4294 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.51833 | 2883.4146 | 4023.9652 | Average | 0.426 | 2614.0105 | 512.9996 | Average | 0.934 | 3870.5792 | 2110.0032 | Average | 0.546 | 2959.3671 | 1613.2661
Duct Area: | 1.3956 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 6 | 0.19625 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514