SL SERIES

(SL AND SL-HR MODELS)

# CARTRIDGE COLLECTOR

# Installation, Operating

& Maintenance Manual

## CONTENTS

DESCRIPTION                                               	1

RECEIVING                                                   	2

COLLECTOR ASSEMBLY                                 	3

DIFFERENTIAL PRESSURE GAUGE ASSEMBLY   	3

BAG ASSEMBLY                                             4

SYSTEM START-UP                                        	4

COMPRESSED AIR REQUIREMENTS                 	5

ELECTRICAL REQUIREMENTS                         	5

OPERATING INSTRUCTIONS                          	6

AUTOMATIC DRAIN                                      	6

THE TIMER                                                   	7

DIFFERENTIAL PRESSURE GAUGE                   	8

DUST DISCHARGE CONFIGURATIONS             	9

START-UP CHECKLIST                                   	10

MAINTENANCE                                             	11

TROUBLESHOOTING                                     	11

SIDE LOAD CARTRIDGE TYPE DUST COLLECTOR

The cartridge type dust collector is a pulse-jet model.  Cleaning is achieved by back-flushing the filters with short bursts of compressed air, repeated at timed intervals.

The timer board (sequence controller) signals the solenoid valves, which in turn trigger the diaphragm valves.  The diaphragm valves deliver short bursts of compressed air to the purge pipe nozzles.

The nozzles are directed at the cartridge openings.  The air jet is sufficient in volume to dislodge a portion of the “dust cake”, permitting it to settle into the hopper.

The hopper is usually fitted with a slide gate (for 55 gallon drum), air lock, or conveyor, which disposes of the collected material without losing the collector’s negative operating pressure.  A self-dumping hopper can also be added in some installations.

- 1 -

RECEIVING

The collector will arrive in sub-assembled form.    Normally, the fan will ship separately.  Be sure to use sealant when installing.

When unloading, take care not to damage the external components.  The use of spreader bars with lift equipment is recommended.

Note:  With large units be sure to remove any bolt-on shipping braces that were used for safe transport of the bins.

Check foundation locations against collector supports.

In addition to the collector, separate packages will be shipped, either with the collector shipment or separately.  Locate and identify contents.

Please Note:  The actual number of containers may vary depending upon the size and style of the collector.

IMPORTANT NOTE:  THE CARTRIDGES ARE INSTALLED IN THIS UNIT.  AFTER INSTALLATION AND BEFORE STARTUP, THE DOORS WILL REQUIRE ONE OR TWO ADDITIONAL TURNS TO ENSURE DOOR GASKET AND OUTSIDE DOOR ARE TIGHT.  HAND TIGHTEN ONLY.  DO NOT OVERTIGHTEN.

ARRANGEMENT DRAWING

WIRING DIAGRAM

INSTALLATION/OPERATING INSTRUCTIONS

INSTALLATION INSTRUCTIONS – Be sure to read all instructions carefully.

HARDWARE PACKAGE – Make sure all items are included with shipment.

SEALANT

COLLECTOR ASSEMBLY FASTENERS

CAGES

DIFFERENTIAL PRESSURE GAUGE

- 2 -

COLLECTOR ASSEMBLY

Orientation should be established before raising the collector to assembly position.  The use of spreader bars with lift equipment is recommended.  Cartridges are already installed in the collector, so care must be used during collector installation.

Apply sealant to the mating flanges.  Hint:  After installation, check for any leaks at flange joints using a plastic bag.  With the fan on, run the plastic over the joints to see if there is any positive or negative air leakage.

It is important for long term operation and bag life that any leaks in the components/ductwork be sealed.

The collector must be level.  Shim and grout as necessary when placing the hopper section on the foundation.  Foundation bolts are not included.

Ladder access and platform/railing access is provided as an option.  See arrangement drawing for instructions. Hardware for these items is usually included in the hardware bag.

### DIFFERENTIAL PRESSURE GAUGE INSTALLATION

Provisions for line attachment have already been made on the collector.

The gauge is mounted and functioning.

IMPORTANT NOTE:  Be sure to remove clean out cap to remove any accumulated dust on a regular basis. This will ensure an accurate gauge reading.

- 3 -

CARTRIDGE ASSEMBLY

The cartridges are positioned on a support assembly and held in position by the door assembly.

When replacing cartridges, the side with the gasket should go in first.  Both front and rear cartridges are interchangeable, so install the second cartridge right behind the first cartridge.

The door assembly is made up of an outer plate and an inner plate.  The inner plate will seal the back end of the second cartridge.  Be sure to handle the door assembly carefully so as not to damage the seals on both plates.  Clean cartridge seals and mating surfaces with a damp rag.

The door assembly consists of two plates with a spring between them.  Position the door assembly over the threaded rod of the support structure.  Then put the knob on and turn until the outer plate is tight against the collector wall.

DO NOT OVERTIGHTEN.  The door seal should compress tightly against the collector wall and the gasket material should compress about 1/16th of an inch.

The spring will apply a pressure against the two cartridges so as to keep the cartridges sealed tightly.

### SYSTEM START-UP

Please be sure to follow system start-up checklist on page 10. This will ensure a proper start-up of your dust collector. PLEASE NOTE IMPORTANT START-UP PROCEDURE: One of the recommended start-up procedures in this checklist is to damper the filtering fan air and slowly introduce the dust load.  This will allow a suitable dust cake on the outside of the bag to be built up slowly and greatly reduce the possibility of blinding the bags.  This reduced air flow adjustment usually takes 6 to 8 hours, depending upon the dust load.  The benefit in doing this will be extended bag life.  After the magnehelic gauge reading has increased by approximately one-half inch of W.C., the fan air can be set at its designed position.

- 4 -

### COMPRESSED AIR REQUIREMENTS

Compressed air requirements are listed on the assembly drawing in SCFM and pressure specifications.

The air supply must be clean, dry and oil free at 90-100 psig.  At a minimum, an air filter and regulator should be installed.  An air dryer is strongly recommended. The drier the compressed air, the longer the bag life.

The air supply line should be 1 inch minimum.

The size of the coupling connection to the manifold tank will depend on the valve size.  For example,

a 3/4" valve will have a 3/4" coupling

a 1" valve will have a 1" coupling

a 1-1/2" valve will have a 1-1/2" coupling

A pressure gauge should be added to the air line immediately before the manifold coupling. It should be regulated to 100 psi since air pressure over 120 psi can damage the air valve diaphragms.

Note:  Recovery to 90-100 psig between pulses is required for proper filter cleaning and extended bag life.

Note:  The drain plug should be removed on a regular basis to allow any moisture in the air tank to drain.  For accessibility and ease of draining, it is recommended that a length of pipe and a ball valve be attached to the drain.

| ### SPECIAL NOTE: | ### To avoid blinding during initial startup of the system or when replacing cartridges, be sure to adjust the filtering air fan damper to approximately ¾ open and introduce dust slowly in order to build up some pressure drop before fully opening the damper to the rated volume. |
| --- | --- |

### ELECTRICAL REQUIREMENTS

The electrical supply for the timer board is to be 120V-60 cycle, single phase.  See wiring diagram below.

The cleaning system must be in operation at all times when the filtering air system is in use.

The cleaning system should also be operable without activating the filtering air fan.  This enables the operator to do “off-line” cleaning, if required.

- 5 -

OPERATING INSTRUCTIONS

It is important that at no time is the collector to be “on-line” without activating the cleaning system.  Automatic “off-time” cleaning system control switches normally activated by pressure changes are not recommended without carefully monitoring to be certain switch limits are always set properly.

The timer is of prime importance to efficient, trouble-free operation.  The operator must see to it that the settings are properly adjusted.  Failure to do so may severely limit the collector’s ability to perform and/or cause frequent maintenance intervals.  The factory has preset the timer for average conditions.  Readjustment is normally a one time requirement, completed at installation start-up.

On outside installations, ice can form in lines and cause valve malfunction.  Application of an air dryer or provisions for auxiliary heat may be made.  If heat is used, do not exceed 180° at the valves.

Maximum filtered air stream temperature is to be 170° without special collector modifications.

### AUTOMATIC DRAIN

In installations where compressed air moisture is present, an automatic drain can be added as shown.  This drain automatically opens at the same time the valve fires.  When it momentarily vents to atmosphere, moisture inside the manifold tank is expelled.  The total length of this drain is four and a half inches long including both close nipples.

- 6 -

THE TIMER

The timer has two functions.  It regulates the cleaning jet bursts in time lapsed per burst (“on-time”) and it controls the time intervals between bursts (“off-time”).

“On-time” determines the time lapse per burst.  It is preset by the factory at 0.10 seconds.  This is a standard setting for most Scientific Dust Collectors.  This setting must remain unchanged.  It is related to valve function, having nothing to do with dust characteristics.  Changing this setting without discussing the change with the factory may negatively affect collector performance and bag life.

“Off-time” regulates the amount of dust accumulation between bursts.  The longer the off time interval, the thicker the dust cake becomes.  The thicker the dust cake becomes, the greater the restriction of air flow through the media.  The increased restriction registers on the differential pressure gauge as increased differential pressure between the clean and dirty air plenums.  Too much cleaning will knock off all the dust cake.  When this occurs, some blow through after pulsing can occur.  Building and maintaining a dust cake at optimum thickness is the objective in achieving dust collector efficiency.

### TIMER SETTING

The “off-time” timer board settings vary, depending on the number of “off-time” positions provided and on the dust load being introduced to the media.

The “off-time” setting from the factory is 30 seconds.  That means that a valve will “fire” and pulse clean one row of bags every 30 seconds.  For most dust loads this is a typical setting.  However, if the dust load is heavy, a setting in the range of 10-20 seconds may be necessary.  There is a correlation between the system pressure drop and the timer board setting.  There is also a correlation between compressed air consumption and the timer board setting.  Adjust the timer’s “off-time” to achieve a stabilized operating condition between 1-3 inches, if possible.

- 7 -

If the “off-time” setting is at 30 seconds and the pressure drop is less than one inch, do not change the setting.  If the pressure drop is more than 3 inches, reduce the “off-time” setting from thirty seconds to twenty-five seconds.  This will shorten the interval between pulses and clean more often.  When this is done, allow 4 to 8 hours to determine if the increased cleaning has helped.  If necessary, continue to reduce the “off-time” setting to achieve a stabilized operating condition.

### THE DIFFERENTIAL PRESSURE GAUGE

The differential pressure gauge registers in units of measure called “inches of water gauge”.

It registers the difference in pressure between the clean and dirty sides of the filtering media.

A record of the readings must be kept, beginning with a reading taken when the filtering media is new, before dust accumulates.

As dust accumulates, the readings will increase over the original “clean” reading between .50 and 6.0 inches water gauge.  The typical reading will be 1-3 inches water gauge.

Adjust the timer’s “off-time” to achieve a stabilized operating condition between 1-3 inches, if possible.  Individual applications may require a higher stabilized reading.  Up to 6 inches water gauge is acceptable.  Beyond that, review the troubleshooting section.

- 8 -

DUST DISCHARGE CONFIGURATIONS

In addition to the Rotary Airlock discharge as illustrated on page 1, there are several other options for discharging dust from the collector.  The most common method is to use a slide gate and drum lid adapter.  During normal operation of the collector, the slide gate remains in the open (outward) position.  To change the drum, the slide gate is pushed in (closed position).  This maintains the negative pressure and will stop dust from passing through. The 55 gallon drum can then be changed while the collector is still running.

Another discharge container is a 3 cubic yard self-dumping hopper.  This is the equivalent size of about six 55 gallon drums.  The quick release clamp is disengaged in order to remove and empty the hopper bin.  When this is done, the collector must be off since a negative pressure is not maintained during this changeover time.

- 9 -

START-UP CHECKLIST

Check the following items in sequence:

Check electrical supply and connections per wiring diagram.

Inspect ductwork and gates for proper positions.

Check to make sure cartridge doors are tight.  Do not overtighten.

Check housing joints assembly and foundation anchors.

See if compressed air supply is regulated to 90-100 psig at the manifold.

Activate the timer.  Check sequence of valve operation.

Check for air pressure recovery between pulses at the manifold (90-100 psig).

Check  for air pressure drop at the manifold, during the pulses.  Not to drop below 45 psig.

Close all access doors.  Check for seal integrity.

Check discharge configuration for seal integrity (conveyor/airlock).

Adjust filtering air fan damper to between 1/2  and 3/4 open.

Activate the filtering air fan, without introducing the dust load.

Record the start-up differential pressure gauge reading, before introducing the dust load.  Reading is __________.

Slowly introduce the dust load.  When the differential pressure gauge indicates a change, sufficient “cake” will have been accumulated to resist media blinding.  Readjust the fan damper to design specifications.

Record stabilized pressure gauge reading.  Reading is __________.  Monitor the differential pressure gauge readings.  Adjust “off-time” timer settings as required.

NOTE:	TROUBLESHOOTING BEGINS WITH A REVIEW OF THE RECORDED DIFFERENTIAL PRESSURE GAUGE READINGS.  IT IS IMPORTANT THAT CLEAN-START VALUES BE RECORDED AS WELL AS THE OPERATING DATA!

- 10 -

MAINTENANCE

Once properly adjusted, the collector requires little maintenance.  The units should be inspected at 3 month intervals as follows:

Note the differential pressure gauge reading and add to your record.  Severe applications may require more frequent checks (weekly or daily).

Check the cleaning air supply for cleanliness and moisture.

Drain any accumulated moisture from the manifold tank.

Empty the dust trap.

Note the operating air pressure gauge readings at the manifold.  Must recover to 90-100 psig between pulses.

Check the air valves for sequential operation.

Check the door and cover seals for leaks.

Refer to Assembly and Start Up Sections for filter replacement.

### TROUBLESHOOTING

Problems with the collector usually appear soon after installation, often the result of improper assembly or operating techniques.  Adhering to the instruction materials in this manual will pay dividends in trouble free operation and extend service intervals.

The collector has been sized for specific conditions, such as moisture and dust characteristics.  Occasionally deviations from the original design parameters will be introduced.  In some instances, the new conditions can be compensated for by substituting special media.  This should only be considered after a thorough analysis of the problem has been made.

Troubleshooting should begin with a review of the start-up checklist.  Normally, the cause of the problem will be within the scope of that list.

The following list is provided as a supplement to the start-up checklist.  It covers a wider range of symptoms and their causes.

- 11 -

| #### SYMPTOM | #### CAUSE | #### ACTION |
| --- | --- | --- |
| Fan stopped | Overload Switch | Electrical supply/rating Drive sheaves reversed Improperly adjusted sheaves Improperly adjusted dampers System differential pressure low Discharge equipment failure |
| Poor hood control | Fan Malfunction | Sheaves reversed Belts slipping Defective fan wheels Incorrect sizing – fan |
|  | Duct System | Incorrect sizing – ducts Incorrect damper position setting Incorrect blast gate setting |
|  | Pressure Differential High | See excessive pressure differential |
| Excessive pressure differential | Cleaning System | Gauge lines plugged Insufficient cleaning air Timer – fuse/board malfunction Valve malfunction Solenoid malfunction |
|  | Plugged Media | Free moisture in air stream Liquid hydrocarbons Overloading Hygroscopic dust Hopper bridging Cleaning system malfunction |
| Compressed air constantly running | Stuck Valve | Check for solenoid valve malfunctions (turn power off and on again to see if solenoid resets). Check for diaphragm valve failure. |
|  | Undersized Air Compressor | Check with compressor manufacturer |

- 12 -