Date: 	5/28/09	     Project#: Absolents           IAQ Crew Leader:  Bill Boisvert

Customer:	Kennametal					Installation:

100 Kennametal Drive			Service:

Weldon, NC 27890				Warranty: X

Mike France					Repair:

# Scope Of Project

- Reinstalled filter wash unit on ODF-4000

  - Set timers to wash for 2 min. every 4 hours.

- Installed washed first stage filter in one unit of the four unit cluster.

  - Unit reading after filter change all in green

  - Found unit with one first stage filter removed

- Washed remainder of first stage filters on all water based coolant units (except unit with wash system)

  - Total of 8 units serviced

  - All units returned to first stage reads of approximately 200 PA

  - Left two washed filter in outside building.

- Placed wash water in two 55 gal. Drums.

- Cleaned units.

Note:  Unit with wash system had not changed in the time that we had removed the wash system (system turned off several days earlier) and filter showed no increase in dp.  You may be able the turn off the system and only turn it on as needed when the dp reaches 300 to 400PA.  If can be turned back off when the filter return to 200 PA.

Please print this report sign and fax back to our office

Thanks,

Bill Boisvert, Project Manager, IAQ

CUSTOMER REMARKS:

CUSTOMER SIGNATURE:						DATE:

TITLE OR DEPARTMENT: