## Current Situation
Profilform Dust Collector Air Flow Measurement 5/15/03
Les Oakley
Velocity Pressure | Velocity
inwc | ft/min
0.65 | 3229
0.62 | 3154
0.77 | 3514
0.94 | 3883
1.2 | 4387
1.27 | 4513
1.3 | 4566
1.3 | 4566
1.3 | 4566
1.3 | 4566
1.32 | 4601
1.25 | 4478
50023
Average | 4168.5833
cfm | 9095.8488 | cfm
Static Pressure | 6.5 | inwc | add 2 inwc for the rest of the system and we have 8.5 inwc total S.P.
Bob, per the original spec and the spec sheet you sent me, this unit is supposed to perform
at 12,000 cfm at 10". As you can see, it is not performing at this level. Can we do a tach reading on the fan to
see if we can get some more flow out of it
Note on C22: : multiplied by 2.182(area in sf for 20 inch duct)