Customer:	Sheppard AFB

822 Ave F Bldg. 825

Sheppard AFB, TX 76311

Contact:	Steve Halloway

Phone: 	 940-676-3539

Email:	 Steve.Halloway@sheppard.af.mil

Date:  9/21/10

Project #: Welding Booths

Sales Order #: Training & Inspection

Serial #: Various

Model #: TMC-7-4

OE Crew:

SCOPE OF PROJECT:        (Installation) – (Service – Warranty) – Demo – Delivery - Engineering

Training was conducted for operation of Model TMC-7-4 Welding Booth. This training involved members of the US Air Force and training center personal.  All units were inspected for proper operation.  Results of this inspection are listed below.  For the purpose of this inspection the serial number use in the serial number on the control panel of the units.  Refer to the layout drawing for unit numbers.

- Unit # 1 –Serial Number 102402

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit # 2 –Serial Number 102409

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit # 3 –Serial Number 102409

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit # 4 –Serial Number 102403

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit # 5 –Serial Number 102404

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit # 6 –Serial Number 102408

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit # 7 –Serial Number 102401

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit # 8 –Serial Number 102405

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit # 9 –Serial Number 102407

  - Found fan contactor inoperative, fan rotation could not be verified.

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit #10 – Serial Number 101502

  - Fan rotation found wrong, corrected

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit #11 – Serial Number 101602

  - Fan rotation found wrong, corrected

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit #12 – Serial Number 101602

  - Fan rotation found wrong, corrected

  - Timer board operation correct

  - Operating controls all correct

  - Set air to .55MPa

- Unit #13 – Serial Number 101401

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to 70psi

- Unit #14 – Serial Number 101402

  - Fan rotation found wrong, corrected

  - Timer board operation correct

  - Operating controls all correct

  - Set air to 70psi

- Unit #15 – Serial Number 101503

  - Fan rotation found wrong, corrected

  - Timer board operation correct

  - Operating controls all correct

  - Set air to 70psi

- Unit #16 – Serial Number 101601

  - Fan rotation found wrong, corrected

  - Timer board operation correct

  - Operating controls found to have problem with two switches in right hand booth, ON/OFF switch was wired to one of the pulse valves and the top pulse valve switch was wired to ON/OFF function. This was corrected. Left unit with all controls operating correctly.

  - Set air to 70psi

- Unit #17 – Serial Number 101403

  - Fan rotation correct

  - Timer board operation correct

  - Operating controls all correct

  - Set air to 70psi

- Unit #18 – Serial Number 101501

  - Fan rotation found wrong, corrected

  - Timer board operation correct

  - Operating controls all correct

  - Set air to 70psi

Please review, print, and make any comments, sign and fax to Oskar office.

Thanks,

Bill Boisvert - Cell (919) 971-3910

Project Manager – Oskar Environmental

E-mail bill.boisvert@oskarsales.com

CUST0MER REMARKS: _____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________