Date: 	1/12/10	  Project#: Greenville Tech. 		OAP Crew: Bill Boisvert

Customer:	Greenville Tech.				Installation: X

Service:

Warranty:

Repair:

# Scope Of Project

- Booth Collector

  - Installed Photohelic Gauge to side of pulse panel.

  - Added new three way switch to panel

  - Wired photohelic and switch into system

  - Removed megnahelic gauge from system

  - Moved gauge lined to other side of unit and connected to new gauge.

  - Tested system – Sat.

  - Reset pulse off time to 30 sec.

  - Tested all 8 valves

    - Valve Number 1 would not reseat.

    - Disassembled valve, cleaned all diaphragms and seating surfaces.

    - Reassembled valve – Tested sat.

  - Unit had a reading of 1.8”WC

    - Set low set point at 2.6”WC

    - Set high level set point at 3.6”WC

  - Sealed holes in collector from gauge line removal.

- Grinding Room Collector

  - Installed Photohelic Gauge to side of pulse panel.

  - Added new three way switch to panel

  - Wired photohelic and switch into system

  - Removed megnahelic gauge from system

  - Moved gauge lined to other side of unit and connected to new gauge.

  - Tested system – Sat.

  - Reset pulse off time to 30 sec.

  - Tested all 6 valves – all sat.

  - Unit had a reading of 1.8”WC

    - Set low set point at 2.6”WC

    - Set high level set point at 3.6”WC

  - Sealed holes in collector from gauge line removal.

Left both panels in the automatic mode and main power off.

Bill Boisvert – Project Manager

Cell - 919-971-3910

Office - 919-562-7181 x219

CUSTOMER REMARKS:

CUSTOMER SIGNATURE:						DATE:

TITLE OR DEPARTMENT: