Date: 	11/25/09	       Project: Greenville Tech. 	OAP Crew:  Bill Boisvert

Customer:	Greenville Tech.				Installation:  X

Greenville, SC					Service:

Warranty:

Repair:

# Scope Of Project

- Grinding Table Collector System

  - Found incorrect control panels install on this system.

    - 50hp panel installed instead of 40hp panel – corrected by electricians.

  - Ensured all clamps had safety lock pins.

  - Checked fan rotation, Found running in wrong direction, had it corrected.

  - Checked operation of Summer/Winter Switch.

    - Roof damper worked correctly

    - Diverter valve did not operate.

      - Had to adjust air cylinder bleed valves to get to cylinder to operate.

      - Found control wiring incorrect. I corrected it.

      - Damper and diverter Valve work correctly.

  - During walk down it was noted that system had no air flow control damper. Will need to add.

  - System had good air flow – 550 f/m at all areas of intake grid.

- Welding Booth System

  - Found incorrect control panels install on this system.

    - 40hp panel installed instead of 50hp panel – corrected by electricians.

  - Ensured all clamps had safety lock pins.

  - Checked fan rotation, Found running in wrong direction, had it corrected.

  - Checked operation of Summer/Winter Switch.

    - All three of the roof dampers did not operate.

      - Note: Panel was designed with a separate control contact for each roof damper.  Electricians wired all dampers together through one contact.  If contact fails at a later date Oskar will not be responsible for repair of the relay.

    - Diverter valve did not operate.

      - Had to adjust air cylinder bleed valves to get to cylinder to operate.

      - Found control wiring incorrect. I corrected it.

      - Damper and diverter Valve work correctly

  - Check air flow at several arms and found air flow consistent at approx.  2200 f/m with all 40 arm open fully.

- Sealed square return air duct.

- Removed at pallets and cardboard from collector are.

CUSTOMER REMARKS:

CUSTOMER SIGNATURE:						DATE:

TITLE OR DEPARTMENT: