May 10, 2010

TRW AUTOMOTIVE

7500 Highway 11 W

Rogersville, TN 37857

Attention:	Ms. Susan Wilson

Mr. Jeremy Pike

Mr. Alan Gilot

Subject:		Factory Start-up Report.

TRW Team:

The unit installation looks great and the units are performing as expected (see results below).  I would highly recommend that the drain plumbing p-traps be completed ASAP to ensure draining online without shutting the unit down.  This will avoid build-up in the plenum or over-flowing.

Start-up report as follows:

Overall Ambient		0.034 mg/m3

ODF-2000

S/N #20090021

- Inlet 		0.0241 mg/m3

- Stage 1		0.155 mg/m3

- Stage 2		0.035 mg/m3

- Stage 3		0.003 mg/m3

Pressure Drop

- Stage 1		0.50” IN WG

- Stage 2		0.50” IN WG

- Stage 3		0.50” IN WG

ODR-2000

S/N #20090411

- Inlet 		35 mg/m3

- Stage 1		7.15 mg/m3

- Stage 2		0.239 mg/m3

- Stage 3		0.000 mg/m3

Pressure Drop

- Stage 1		0.50” IN WG

- Stage 2		1.0” IN WG

- Stage 3		1.0” IN WG

ODR-2000

S/N #20090371

NOT RUNNING

Pressure Drop

- Stage 1		1.0” IN WG

- Stage 2		0.75” IN WG

- Stage 3		0.75” IN WG

ODF-800

S/N #20090351

NOT RUNNING

ODF-2000

S/N #2009005

- Inlet 		6.43 mg/m3

- Stage 1		1.18 mg/m3

- Stage 2		0.09 mg/m3

- Stage 3		0.006 mg/m3

Pressure Drop

- Stage 1		1.0” IN WG

- Stage 2		0.85” IN WG

- Stage 3		0.25” IN WG

Note: Second stage Minihelic® gauge changed out during site visit.

ODF-2000

S/N #2009026

NOT RUNNING

Pressure Drop

- Stage 1		0.50” IN WG

- Stage 2		0.50” IN WG

- Stage 3		0.50” IN WG

ODF-1000C

S/N #20090365

NOT RUNNING

Pressure Drop

- Stage 1		0.25” IN WG

- Stage 2		0.25” IN WG

ODF-1000C

S/N #20090364

- Exhaust

- (Stage 2)	0.00 mg/m3

Pressure Drop

- Stage 1		0.50” IN WG

- Stage 2		0.50” IN WG

Please review and do not hesitate to call with questions.

I will return to cover the units where the process was not running during my inspection.

Best regards,

Ken Haga

SE Territory Manager

Oskar Environmental, Inc./Industrial Air Quality

Mobile: 919.971.1943

NC Corporate Office: 919.570.2862

NC Corporate Fax: 919.570.2863

Email: khaga@oskarsales.com

Web Site: www.oskarsales.com