| Regional SE IAQ Office for FL, GA, & TN | Corporate Office: |
| --- | --- |
| Email: khaga@iaqsales.com | 95 Cypress Drive |
| GA Office Phone: 678.454.0316 | Youngsville, NC 27596 |
| GA Fax: 678.454.0317 | NC Office: 919.562.7181۰Fax: 919.562.7182 |
| Mobile Phone: 919.971.1943 | www.industrialairquality.com |
| NC IAQ Corporate Toll-free: 800.232.9559 |  |

April 9, 2007

TRW FUJI VALVE, INC.							Office: 865.428.8453

128 River Bend Drive							Fax: 865.428.8499

Sevierville, TN 37876

Attention:	Mr. Christopher Payne

Mr. Jim West

Subject:		Absolent Mist Collection System Performance.

Gentlemen:

The following reflects observations/readings taken during my site visit from last Friday:

Department 40A Mist Collector – ODF-2000S

| Reading Location | Aerosol Samples Min./Avg./Max. | Pressure Drop |
| --- | --- | --- |
| Inlet | 125/89/159 mg/m3 | NA |
| Stage I Fiber Bed Filter | 66/77/117 mg/m3 | 0.8” IN WG |
| Stage II Fiber Bed Filter | 60.8/46/71 mg/m3 | 0.5” IN WG |
| HEPA Filter Stage | 12.0 mg/m3 | 0.04 PSI |

Notes:

- Inspect P-trap for proper set-up

- Ductwork modification is required

- Re-evaluate system for ODF filter selection & application

- System is ducted to (4) MUG grinders

Department 60D Mist Collector – ODF-2000S

| Reading Location | Aerosol Samples Min./Avg./Max. | Pressure Drop |
| --- | --- | --- |
| Inlet | 114/99/126 mg/m3 | NA |
| Stage I Fiber Bed Filter | 88/65/123 mg/m3 | Gauges Require Inspection |
| Stage II Fiber Bed Filter | 69.9/59.3/84 mg/m3 | Gauges Require Inspection |
| HEPA Filter Stage | 6.239 mg/m3 | Gauges Require Inspection |

Notes:

- No P-trap

- Ductwork modification is required

- Re-evaluate system for ODF filter selection & application

- System is ducted to (3) MUG grinders with long ductwork runs

Department 45A Mist Collector – ODF-2000S

| Reading Location | Aerosol Samples Min./Avg./Max. | Pressure Drop |
| --- | --- | --- |
| Inlet | 112/76/150 mg/m3 | NA |
| Stage I Fiber Bed Filter | 42/28/68 mg/m3 | 2.0” IN WG |
| Stage II Fiber Bed Filter | 2.2/1.1/3.7 mg/m3 | 2.0” IN WG |
| HEPA Filter Stage | 3.3/2.65/3.7 mg/m3 0.236 mg/m3 outlet of HEPA | 0.6” IN WG |

Notes:

- Inspect P-trap for proper set-up

- Ductwork modification is required (clamp off and two duct runs off of plenum)

- System is ducted to (2) MUG grinders and (1) COS (grind/cut-off machine)

- Re-evaluate system for ODF filter selection & application

Department 60H/S Mist Collector – ODF-2000S

| Reading Location | Aerosol Samples Min./Avg./Max. | Pressure Drop |
| --- | --- | --- |
| Inlet | 135/120/150 mg/m3 | NA |
| Stage I Fiber Bed Filter | 30/27.6/35 mg/m3 | 0.85” IN WG |
| Stage II Fiber Bed Filter | 14/14/16.1 mg/m3 | 2.0” IN WG |
| HEPA Filter Stage | 0.233 mg/m3 outlet of HEPA | 0.4” IN WG |

Notes:

- P-trap appears to have the proper configuration

- Ductwork configuration appears to be acceptable

- System is ducted to (2) MUG grinders

- Re-evaluate system for ODF filter selection & application

Additional Notes & Conclusion/Summary:

  - ODR-3000 system inspected and fan rotation was incorrect.

    - System repaired and functioning properly during visit.

    - Inspect drain/pump system for float control cleaning as required.

    - Pull filter efficiency data to compare against ODF-2000/S/MOD.

  - Next visit test system and drop airflow (volume) on systems.

  - Inspect machines for cavity dimensions, access door dimensions, and determine standards for TRW for airflow and system selection chart.

  - Inspect random filter gaskets for potential bypass (reference department 40A mist collector).

  - Thorough system inspection of facility mist collectors.

  - A large portion of the mist collector inlet concentration samples exceed Absolent’s filter selection guidelines.

Please review my notes and do not hesitate to call or reply with questions and or comments.

Best regards,

Ken Haga/IAQ

Cc: IAQ Team.