## Planet Pin
|  | Location # | Main Header
|  | Test Point | VP | V | CFM
|  | 1 | 0.63 | 3178.8702 | 1109.0725 |  |  | ODR-2000
|  | 2 | 0.64 | 3204 | 1117.84 |  |  | SN:20060298
|  | 3 | 0.37 | 2436.1464 | 849.9444 |  |  | !st. Stage - 600Pa
|  | 4 | 0.63 | 3178.8702 | 1109.0725 |  |  | HEPA - 200Pa
|  | 5 | 0.5 | 2831.9627 | 988.0403
|  | 6 |  | 0 | 0
|  | 7 |  | 0 | 0
|  | 8 |  | 0 | 0
|  | 9 |  | 0 | 0
|  | 10 |  | 0 | 0
|  | 11 |  | 0 | 0
|  | 12 |  | 0 | 0
|  | 13 |  | 0 | 0
|  | 14 |  | 0 | 0
|  | 15 |  | 0 | 0
|  | Average | 0.554 | 2980.9686 | 1040.0268
|  | Duct Area: | 0.34889
|  | Length | Width | Area SF
0
Diameter
|  |  | 8 | 0.34889
Location # | Machice #3 |  |  |  | Location # | Machice #4
Test Point | VP | V | CFM |  | Test Point | VP | V | CFM
1 | 0.16 | 1602 | 314.3925 |  | 1 | 0.13 | 1444.0233 | 283.3896
2 | 0.13 | 1444.0233 | 283.3896 |  | 2 | 0.14 | 1498.5338 | 294.0873
3 | 0.14 | 1498.5338 | 294.0873 |  | 3 | 0.14 | 1498.5338 | 294.0873
4 | 0.14 | 1498.5338 | 294.0873 |  | 4 | 0.17 | 1651.3038 | 324.0684
5 |  | 0 | 0 |  | 5 |  | 0 | 0
6 |  | 0 | 0 |  | 6 |  | 0 | 0
7 |  | 0 | 0 |  | 7 |  | 0 | 0
8 |  | 0 | 0 |  | 8 |  | 0 | 0
9 |  | 0 | 0 |  | 9 |  | 0 | 0
10 |  | 0 | 0 |  | 10 |  | 0 | 0
11 |  | 0 | 0 |  | 11 |  | 0 | 0
12 |  | 0 | 0 |  | 12 |  | 0 | 0
13 |  | 0 | 0 |  | 13 |  | 0 | 0
14 |  | 0 | 0 |  | 14 |  | 0 | 0
15 |  | 0 | 0 |  | 15 |  | 0 | 0
Average | 0.1425 | 1511.8543 | 296.7014 |  | Average | 0.145 | 1525.0586 | 299.2927
Duct Area: | 0.19625 |  |  |  | Duct Area: | 0.19625
Length | Width | Area SF |  |  | Length | Width | Area SF
|  | 0 |  |  |  |  | 0
| Diameter |  |  |  |  | Diameter
| 6 | 0.19625 |  |  |  | 6 | 0.19625
Location # | Machine #5 |  |  |  | Location # | Machine #6
Test Point | VP | V | CFM |  | Test Point | VP | V | CFM
1 | 0.11 | 1328.3082 | 260.6805 |  | 1 | 0.1 | 1266.4922 | 248.5491
2 | 0.12 | 1387.3727 | 272.2719 |  | 2 | 0.13 | 1444.0233 | 283.3896
3 | 0.1 | 1266.4922 | 248.5491 |  | 3 | 0.12 | 1387.3727 | 272.2719
4 | 0.12 | 1387.3727 | 272.2719 |  | 4 | 0.12 | 1387.3727 | 272.2719
5 |  | 0 | 0 |  | 5 |  | 0 | 0
6 |  | 0 | 0 |  | 6 |  | 0 | 0
7 |  | 0 | 0 |  | 7 |  | 0 | 0
8 |  | 0 | 0 |  | 8 |  | 0 | 0
9 |  | 0 | 0 |  | 9 |  | 0 | 0
10 |  | 0 | 0 |  | 10 |  | 0 | 0
11 |  | 0 | 0 |  | 11 |  | 0 | 0
12 |  | 0 | 0 |  | 12 |  | 0 | 0
13 |  | 0 | 0 |  | 13 |  | 0 | 0
14 |  | 0 | 0 |  | 14 |  | 0 | 0
15 |  | 0 | 0 |  | 15 |  | 0 | 0
Average | 0.1125 | 1343.3178 | 263.6261 |  | Average | 0.1175 | 1372.8448 | 269.4208
Duct Area: | 0.19625 |  |  |  | Duct Area: | 0.19625
Length | Width | Area SF |  |  | Length | Width | Area SF
|  | 0 |  |  |  |  | 0
| Diameter |  |  |  |  | Diameter
| 6 | 0.19625 |  |  |  | 6 | 0.19625

## Planetary #3
Location # | Maim Header |  |  | Location # | Machine # 3 drop
Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.53 | 2915.684 | 1017.2498 | 1 | 0.33 | 2300.6973 | 451.5119
2 | 0.56 | 2997.0676 | 1045.6436 | 2 | 0.45 | 2686.6357 | 527.2523
3 | 0.59 | 3076.2989 | 1073.2865 | 3 | 0.44 | 2656.6165 | 521.361
4 | 0.59 | 3076.2989 | 1073.2865 | 4 | 0.43 | 2626.2541 | 515.4024
5 | 0.5 | 2831.9627 | 988.0403 | 5 | 0.39 | 2501.1217 | 490.8451
6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.554 | 2980.9686 | 1040.0268 | Average | 0.408 | 2558.1889 | 502.0446
Duct Area: | 0.34889 |  |  | Duct Area: | 0.19625
Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter
| 8 | 0.34889 |  |  | 6 | 0.19625
ODR-2000
SN: 20060271
1st. Stage - 550Pa
HEPA - 250Pa

## Dynamic Thrust
Location # | Main Header
Test Point | VP | V | CFM
1 | 1.15 | 4294.884 | 1498.4373
2 | 0.9 | 3799.4766 | 1325.5952
3 | 1.1 | 4200.4794 | 1465.5006
4 | 1 | 4005 | 1397.3
5 |  | 0 | 0
6 |  | 0 | 0
7 |  | 0 | 0
8 |  | 0 | 0
9 |  | 0 | 0
10 |  | 0 | 0
11 |  | 0 | 0
12 |  | 0 | 0
13 |  | 0 | 0
14 |  | 0 | 0
15 |  | 0 | 0
Average | 1.0375 | 4079.4026 | 1423.2583
Duct Area: | 0.34889
Length | Width | Area SF
0
Diameter
| 8 | 0.34889
ODF-2000
SN: 20060289
!st. Stage - 300Pa
2nd. Stage - 250Pa
HEPA - 300Pa

## Radial Machines 1-12
Location # | Main Hearder |  |  | Location # | Machines 1&2 |  |  | Location # | Machines 3&4 |  |  | Location # | Machines 5&6
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.74 | 3445.2313 | 1202.0029 | 1 | 0.4 | 2532.9844 | 220.9325 | 1 | 0.41 | 2564.4513 | 223.6771 | 1 | 0.39 | 2501.1217 | 490.8451
2 | 0.73 | 3421.8735 | 1193.8536 | 2 | 0.4 | 2532.9844 | 220.9325 | 2 | 0.42 | 2595.5366 | 226.3885 | 2 | 0.38 | 2468.8478 | 484.5114
3 | 0.75 | 3468.4317 | 1210.0973 | 3 | 0.39 | 2501.1217 | 218.1534 | 3 | 0.41 | 2564.4513 | 223.6771 | 3 | 0.39 | 2501.1217 | 490.8451
4 | 0.74 | 3445.2313 | 1202.0029 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.74 | 3445.2313 | 1202.0029 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.74 | 3445.2313 | 1202.0029 | Average | 0.39667 | 2522.4082 | 220.0101 | Average | 0.41333 | 2574.8548 | 224.5846 | Average | 0.38667 | 2490.4102 | 488.743
Duct Area: | 0.34889 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.19625
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 8 | 0.34889 |  |  | 4 | 0.087222 |  |  | 4 | 0.087222 |  |  | 6 | 0.19625
Location # | Machines 7&8 |  |  | Location # | Machines 9&10 |  |  | Location # | Machines 11&12
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | ODF-2000
1 | 0.36 | 2403 | 209.595 | 1 | 0.29 | 2156.7585 | 188.1173 | 1 | 0.3 | 2193.6288 | 191.3332 |  | SN: 20060290
2 | 0.37 | 2436.1464 | 212.4861 | 2 | 0.34 | 2335.2962 | 203.6897 | 2 | 0.32 | 2265.5701 | 197.6081 |  | !st. Stage - 350Pa
3 | 0.36 | 2403 | 209.595 | 3 | 0.33 | 2300.6973 | 200.6719 | 3 | 0.31 | 2229.8896 | 194.4959 |  | 2nd. Stage - 300Pa
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 |  | HEPA - 250 Pa
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.36333 | 2414.0994 | 210.5631 | Average | 0.32 | 2265.5701 | 197.6081 | Average | 0.31 | 2229.8896 | 194.4959
Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 4 | 0.087222 |  |  | 4 | 0.087222 |  |  | 4 | 0.087222

## Radial Machines 13-24
Location # | Main Hearder |  |  | Location # | Machines13-14 |  |  | Location # | Machines15-16 |  |  | Location # | Machines17-18
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.86 | 3714.0842 | 1295.8027 | 1 | 0.4 | 2532.9844 | 220.9325 | 1 | 0.46 | 2716.3232 | 236.9237 | 1 | 0.46 | 2716.3232 | 533.0784
2 | 0.79 | 3559.7219 | 1241.9474 | 2 | 0.41 | 2564.4513 | 223.6771 | 2 | 0.45 | 2686.6357 | 234.3343 | 2 | 0.46 | 2716.3232 | 533.0784
3 | 0.83 | 3648.7286 | 1273.0009 | 3 | 0.38 | 2468.8478 | 215.3384 | 3 | 0.46 | 2716.3232 | 236.9237 | 3 | 0.44 | 2656.6165 | 521.361
4 | 0.79 | 3559.7219 | 1241.9474 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.86 | 3714.0842 | 1295.8027 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.826 | 3639.9259 | 1269.9297 | Average | 0.39667 | 2522.4082 | 220.0101 | Average | 0.45667 | 2706.4635 | 236.0638 | Average | 0.45333 | 2696.5678 | 529.2014
Duct Area: | 0.34889 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.19625
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 8 | 0.34889 |  |  | 4 | 0.087222 |  |  | 4 | 0.087222 |  |  | 6 | 0.19625
Location # | Machines19-20 |  |  | Location # | Machines21-22 |  |  | Location # | Machines23-24
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | ODF-2000
1 | 0.31 | 2229.8896 | 194.4959 | 1 | 0.31 | 2229.8896 | 194.4959 | 1 | 0.25 | 2002.5 | 174.6625 |  | SN: 20060287
2 | 0.32 | 2265.5701 | 197.6081 | 2 | 0.31 | 2229.8896 | 194.4959 | 2 | 0.28 | 2119.2468 | 184.8454 |  | !st. Stage - 250Pa
3 | 0.29 | 2156.7585 | 188.1173 | 3 | 0.34 | 2335.2962 | 203.6897 | 3 | 0.26 | 2042.1573 | 178.1215 |  | 2nd. Stage - 200Pa
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 |  | HEPA - 300Pa
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.30667 | 2217.8686 | 193.4474 | Average | 0.32 | 2265.5701 | 197.6081 | Average | 0.26333 | 2055.2064 | 179.2597
Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 4 | 0.087222 |  |  | 4 | 0.087222 |  |  | 4 | 0.087222

## Radial Machines 25-36
Location # | Main Hearder |  |  | Location # | Machines 25-26 |  |  | Location # | Machines 27-28 |  |  | Location # | Machines 29-30
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.71 | 3374.673 | 1177.3859 | 1 | 0.46 | 2716.3232 | 236.9237 | 1 | 0.54 | 2943.0619 | 256.7004 | 1 | 0.26 | 2042.1573 | 400.7734
2 | 0.72 | 3398.3552 | 1185.6484 | 2 | 0.43 | 2626.2541 | 229.0677 | 2 | 0.55 | 2970.1875 | 259.0664 | 2 | 0.29 | 2156.7585 | 423.2639
3 | 0.69 | 3326.8029 | 1160.6846 | 3 | 0.47 | 2745.6897 | 239.4852 | 3 | 0.55 | 2970.1875 | 259.0664 | 3 | 0.32 | 2265.5701 | 444.6181
4 | 0.71 | 3374.673 | 1177.3859 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.72 | 3398.3552 | 1185.6484 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.71 | 3374.673 | 1177.3859 | Average | 0.45333 | 2696.5678 | 235.2006 | Average | 0.54667 | 2961.1732 | 258.2801 | Average | 0.29 | 2156.7585 | 423.2639
Duct Area: | 0.34889 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.19625
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 8 | 0.34889 |  |  | 4 | 0.087222 |  |  | 4 | 0.087222 |  |  | 6 | 0.19625
Location # | Machines 31-32 |  |  | Location # | Machines 33-34 |  |  | Location # | Machines 35-36
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | ODF-2000
1 | 0.36 | 2403 | 209.595 | 1 | 0.38 | 2468.8478 | 215.3384 | 1 | 0.31 | 2229.8896 | 194.4959 |  | SN: 20060288
2 | 0.36 | 2403 | 209.595 | 2 | 0.35 | 2369.39 | 206.6635 | 2 | 0.31 | 2229.8896 | 194.4959 |  | !st. Stage - 150Pa
3 | 0.35 | 2369.39 | 206.6635 | 3 | 0.39 | 2501.1217 | 218.1534 | 3 | 0.32 | 2265.5701 | 197.6081 |  | 2nd. Stage - 200Pa
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 |  | HEPA - 200Pa
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.35667 | 2391.8491 | 208.6224 | Average | 0.37333 | 2447.0954 | 213.4411 | Average | 0.31333 | 2241.8462 | 195.5388
Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.087222
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 4 | 0.087222 |  |  | 4 | 0.087222 |  |  | 4 | 0.087222