Customer:	 WEC

401 River Terminal Rd.

Chattanooga, TN 37406

Contact:	Mike Lary

Phone: 	423-697-5024

Email:		larymh@westinghouse.com

Date:  5/3/10

Project #: Warranty Repair

Sales Order #:

Serial #: 091308

Model #: SDC-25X2-40

OE Crew: Bill Boisvert

SCOPE OF PROJECT:         Installation – Service – (Warranty) – Demo – Delivery - Engineering

Problem:

Fan number 2 would not transition from start up mode to run mode.  This caused the motor to trip the over loads.

Fix:

Found that the timer was not transitioning after 20 seconds. Removed timer module from spare collector and installed in SN: 091308.  Fan started normally.

We need the sent Mike a new timer module to be put back into spare collector.

Trip setting where checked and reset as needed.

Mike,

Please review, print, and make any comments, sign and fax to Oskar office.

Thanks,

Bill Boisvert - Cell (919) 971-3910

Project Manager – Oskar Environmental

E-mail bill.boisvert@oskarsales.com

CUST0MER REMARKS: _____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________