Customer:	 WEC – Welding Inst.

401 River Terminal Rd.

Chattanooga, TN 37406

Contact:	 Mike Lary

Phone: 	 803-367-1898

Email:		 larymh@westinghouse.com

Date:  7/1/10

Project #:

Sales Order #:

Serial #:

Model #:

OE Crew:       Bill Boisvert & Dan Kuster

SCOPE OF PROJECT:        Installation – Service – (Warranty) – Demo – Delivery - Engineering

- Dust Collectors

  - Applied duct sealant to all joints on air turn air duct

  - Resealed main joint on all threes collectors

  - Removed loose sound insulation from inlet elbows

  - Emptied all water from three of the six barrels

- Grinding Tables

  - Table #5

    - Fan is out of balance fan

    - No electrical problem found

    - Fuses where vibrating loose

    - Fan was removed for repair

    - Removed loose sound insulation from discharge plenum

  - Table # 3

    - Removed loose sound insulation from discharge plenum

    - No vibration noted

  - Tables #1 & #4

    - No loose sound insulation

    - No vibration noted

  - Table # 2

    - No loose sound insulation

    - Minor vibration noted

- Plasma Table

    - Table needs new V-Cell after filter.  Filer is falling apart.

Note:  No severalof the tables we have gotten minor smoldering of the sound insulation.  We may need to look into availability of a fire retardant insulation for this application.

Please review, print, and make any comments, sign and fax to Oskar office.

Thanks,

Bill Boisvert - Cell (919) 971-3910

Project Manager – Oskar Environmental

E-mail bill.boisvert@oskarsales.com

CUST0MER REMARKS: _____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________