## SHEET1
Date: 7/28/08
Industrial Air Quality Youngsville, NC
Job Number: 14824
System Size and Motor List
System Number | Machine | System Size | Blower Type | Blower Model & Rotation | Location | Blower Speed | Horsepower Req. | Recommended Motor | FLA
T1 | Floor Sweep | 20" | Main Blower | M19 CWUP | Baler Room Floor | 1643 | 36.5 | 50 H.P. | 61
T2 | McKinley 3 Color R\D\C | 20" | Main Blower | M19 CWUP | Baler Room Floor | 1566 | 33.2 | 40 H.P. | 49
T3 | McKinley 1 Color R\D\C | 20" | Main Blower | M19 CWUP | Baler Room Floor | 1682 | 38.7 | 50 H.P. | 61
Air Conveying Corp. will supply the blowers, motors, belt guards and v-belt drives. We will also provide a structural channel support frame to be mounted on isolators provided by others. The blowers will be shipped as assemblies mounted on the frames. The isolators will be mounted to the floor by others. Inlet reducers and discharge transitions or isolators to be provided by others. Installation and electrical starters to be provided by others.