ELECTRICAL REQUIREMENTS

Eurovac provides a control panel for the vacuum system.  Customer is responsible for all high voltage wiring and providing a fused disconnect if required.  Electrical wiring may include the following:

- Wiring from customer’s main supply to fused disconnect and from disconnect to control panel.

- Wiring from control panel to main vacuum pump(s).

- Electrical drawing and system schematics specific to your system will be forwarded to the correct personnel upon request.

ELECTRICAL SPECIFICATIONS

| H.P. | SUPPLY | FULL LOAD | CIRCUIT REQUIRED | EXHAUST HOLE SIZE | CONCRETE LENGTH | PAD SIZE WIDTH | OVERHEAD CLEARANCE |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4 | 230/1/60 | 18 Amps | 25 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 5 | 208-240/3/60 | 17.5-15 Amps | 25 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 5 | 480/3/60 | 7.5 Amps | 15 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 5 | 575/3/60 | 5.8 Amps | 10 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 7 | 208-240/3/60 | 16-15 Amps | 25 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 7 | 480/3/60 | 8 Amps | 15 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 7 | 575/3/60 | 6.7 Amps | 15 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 10 | 208-240/3/60 | 30-27 Amps | 40 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 10 | 480/3/60 | 13 Amps | 20 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 10 | 575/3/60 | 10.5 Amps | 15 Amps | 4 ½” | 5’ | 3’ | 8’ |
| 15 | 208-240/3/60 | 39-37 Amps | 60 Amps | 5 ½” | 8’ | 4’ | 10’ |
| 15 | 480/3/60 | 18 Amps | 30 Amps | 5 ½” | 8’ | 4’ | 10’ |
| 15 | 575/3/60 | 15.8 Amps | 25 Amps | 5 ½” | 8’ | 4’ | 10’ |
| 20 | 208-240/3/60 | 48-44 Amps | 70 Amps | 5 ½” |  |  |  |
| 20 | 480/3/60 | 22 Amps | 40 Amps | 5 ½” |  |  |  |
| 20 | 575/3/60 | 16 Amps | 40 Amps | 5 ½” |  |  |  |
| 10+10 | 208-240/3/60 | 30+30/27+2 A | 80 Amps | 5 ½” | 8’ | 10’ | 12’ |
| 10+10 | 480/3/60 | 13+13 Amps | 40 Amps | 5 ½” | 8’ | 10’ | 12’ |
| 10+10 | 575/3/60 | 10.5+10.5 A | 30 Amps | 5 ½” | 8’ | 10’ | 12’ |

**ALWAYS USE TIME DELAY/SLO-BLO FUSES

- Customer is responsible for all roof/wall penetrations.

- All Compressed air pipe work by others.

- Location and hole sizes to be determined by Installer.

- On certain size systems, the control panel is pre-wired into the pump(s) and the automatic self- cleaning system (if equipped).

- All space requirements based on standard size filter/separator.

- Eurovac strongly recommends exhausting equipment outside.  Problems caused by internal 	exhausting may include; heat, noise and dust.  (Eurovac will supply rain cap anyway).

- A Hepa filter is highly recommended for internal exhausting.