## 701
DUST COLLECTOR PERFORMANCE
Two-Stage 20HP | Max static pressure (inch/H2O) | Max CFM | Hp | Volts | Hz | Impeller | Inlet | Dercibel rating
| 11 | 8000 | 20 | 208V | 60 | Φ26" | Φ16" | 87
| Restrictor plate (inch) | Dia. 16" | Dia. 14" | Dia. 12" | Dia.10" | Dia.8" | Dia. 7" | Dia. 0"
Two-Stage 20HP | Static pressure (Inch/H2O) | 2.87 | 3.63 | 5.46 | 7.93 | 9.8 | 10.5 | 11
| CFM | 8000 | 7565 | 6450 | 5095 | 3402 | 2306 | 0
| Velocity | 2.04 | 1.83 | 1.33 | 0.83 | 0.37 | 0.17 | 0
CFM
STATIC PRESSURE
Remark:
1.The speed meter and static pressure indicator is located in dia 16” x 8 times of the flexible pipe away
from the suction
2. The total length of the flexible pipe is dia 16" x 16 times.
3.The Max C.F.M is measured when the intake is dia. 16" x 1 holes and Max.
Static presure is measured when the diameter of intake port is DIA. 0”.