## Flow Balance
Before Flow Balance
Location # | Machine #1 |  |  | Location # | Machine #2 |  |  |  | Location # | Machine #3 |  |  | Location # | Machine #4 |  |  | Location # | At Absolent Inlet
Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.68 | 3302.6076 | 648.1367 | 1 | 0.45 | 2686.6357 | 527.2523 |  | 1 | 0.72 | 3398.3552 | 666.9272 | 1 | 0.5 | 2831.9627 | 555.7727 | 1 | 0.9 | 3799.4766 | 2982.5891
2 | 0.78 | 3537.1202 | 694.1598 | 2 | 0.51 | 2860.1421 | 561.3029 |  | 2 | 0.92 | 3841.4611 | 753.8867 | 2 | 0.7 | 3350.8234 | 657.5991 | 2 | 0.84 | 3670.6431 | 2881.4549
3 | 0.68 | 3302.6076 | 648.1367 | 3 | 0.5 | 2831.9627 | 555.7727 |  | 3 | 0.85 | 3692.4276 | 724.6389 | 3 | 0.55 | 2970.1875 | 582.8993 | 3 | 0.61 | 3128.005 | 2455.4839
4 |  | 0 | 0 | 4 |  | 0 | 0 |  | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 | 0.6 | 3102.2597 | 2435.2738
5 |  | 0 | 0 | 5 |  | 0 | 0 |  | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 | 0.6 | 3102.2597 | 2435.2738
6 |  | 0 | 0 | 6 |  | 0 | 0 |  | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 |  | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
Average | 0.71333 | 3382.5855 | 663.8324 | Average | 0.48667 | 2793.948 | 548.3123 |  | Average | 0.83 | 3648.7286 | 716.063 | Average | 0.58333 | 3058.8693 | 600.3031 | Average | 0.71 | 3374.673 | 2649.1183
Duct Area: | 0.19625 |  |  | Duct Area: | 0.19625 |  |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.785
Length | Width | Area SF |  | Length | Width | Area SF |  |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 6 | 0.19625 |  |  | 6 | 0.19625 |  |  |  | 6 | 0.19625 |  |  | 6 | 0.19625 |  |  | 12 | 0.785
|  | Dust Track Reading | [11 empty] | Note:
|  | Each machine had counts of about .160 mg/m3 | [5 empty] | Gauge reading (New Gauges, after filer change) |  |  |  |  | New gauges installed have are as follows:
|  | Inlet to Absolent was .160 mg/m3 | [6 empty] | Stage #1 | 300pa |  |  | First Stage - green from 0 - 500pa
|  | Outlet of Absolent was .025 mg/m3 | [6 empty] | Stage #2 | 500pa |  |  | Second Stage - Green from 0 - 500pa
|  | (With old second stage filters) | [6 empty] | HEPA | 300pa |  |  | HEPA - Green from 0 - 600pa
|  | Could not get reading after new second stage | [10 empty] | Old gauges installed are as follows:
|  | due to grinders being shut down. | [10 empty] | First Stage - green from 0 - 500pa
|  | General area readings .031 mg/m3 to .036 mg/m3 | [10 empty] | Second Stage - Green from 0 - 600pa
HEPA - Green from 0 - 600pa
After Flow Balance
Location # | Machine #1 |  |  | Location # | Machine #2 |  |  |  | Location # | Machine #3 |  |  | Location # | Machine #4 |  |  | Location # | At Absolent Inlet
Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.6 | 3102.2597 | 608.8185 | 1 | 0.55 | 2970.1875 | 582.8993 |  | 1 | 0.59 | 3076.2989 | 603.7237 | 1 | 0.5 | 2831.9627 | 555.7727 | 1 | 0.59 | 3076.2989 | 2414.8946
2 | 0.56 | 2997.0676 | 588.1745 | 2 | 0.61 | 3128.005 | 613.871 |  | 2 | 0.61 | 3128.005 | 613.871 | 2 | 0.7 | 3350.8234 | 657.5991 | 2 | 0.6 | 3102.2597 | 2435.2738
3 | 0.59 | 3076.2989 | 603.7237 | 3 | 0.59 | 3076.2989 | 603.7237 |  | 3 | 0.58 | 3050.1171 | 598.5855 | 3 | 0.55 | 2970.1875 | 582.8993 | 3 | 0.54 | 2943.0619 | 2310.3036
4 |  | 0 | 0 | 4 |  | 0 | 0 |  | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 | 0.61 | 3128.005 | 2455.4839
5 |  | 0 | 0 | 5 |  | 0 | 0 |  | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 | 0.58 | 3050.1171 | 2394.3419
6 |  | 0 | 0 | 6 |  | 0 | 0 |  | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 |  | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
Average | 0.58333 | 3058.8693 | 600.3031 | Average | 0.58333 | 3058.8693 | 600.3031 |  | Average | 0.59333 | 3084.9767 | 605.4267 | Average | 0.58333 | 3058.8693 | 600.3031 | Average | 0.584 | 3060.6167 | 2402.5841
Duct Area: | 0.19625 |  |  | Duct Area: | 0.19625 |  |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.785
Length | Width | Area SF |  | Length | Width | Area SF |  |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 6 | 0.19625 |  |  | 6 | 0.19625 |  |  |  | 6 | 0.19625 |  |  | 6 | 0.19625 |  |  | 12 | 0.785

## Sheet3
Location # |  |  |  | Location # |  |  |  | Location # |  |  |  | Location #
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 |  | 0 | 0
2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 |  | 0 | 0
3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 |  | 0 | 0
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0 | 0 | 0 | Average | 0 | 0 | 0 | Average | 0 | 0 | 0 | Average | 0 | 0 | 0
Duct Area: | 0 |  |  | Duct Area: | 0 |  |  | Duct Area: | 0 |  |  | Duct Area: | 0
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # |  |  |  | Location # |  |  |  | Location # |  |  |  | Location #
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 |  | 0 | 0
2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 |  | 0 | 0
3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 |  | 0 | 0
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0 | 0 | 0 | Average | 0 | 0 | 0 | Average | 0 | 0 | 0 | Average | 0 | 0 | 0
Duct Area: | 0 |  |  | Duct Area: | 0 |  |  | Duct Area: | 0 |  |  | Duct Area: | 0
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # |  |  |  | Location # |  |  |  | Location # |  |  |  | Location #
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 |  | 0 | 0
2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 |  | 0 | 0
3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 |  | 0 | 0
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0 | 0 | 0 | Average | 0 | 0 | 0 | Average | 0 | 0 | 0 | Average | 0 | 0 | 0
Duct Area: | 0 |  |  | Duct Area: | 0 |  |  | Duct Area: | 0 |  |  | Duct Area: | 0
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Location # |  |  |  | Location # |  |  |  | Location # |  |  |  | Location #
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | 1 |  | 0 | 0
2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 |  | 0 | 0 | 2 |  | 0 | 0
3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 |  | 0 | 0 | 3 |  | 0 | 0
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0 | 0 | 0 | Average | 0 | 0 | 0 | Average | 0 | 0 | 0 | Average | 0 | 0 | 0
Duct Area: | 0 |  |  | Duct Area: | 0 |  |  | Duct Area: | 0 |  |  | Duct Area: | 0
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0