Coastal Carolina Inspection Report

Inspection Date: 3/6/12

I inspected all arms at Coastal Carolina Community College.  I found that four top flex pieces where collapsed and one middle flex piece was collapsed.  Three other middle flex pieces where marginal.  It is my opinion that all the flex in the top and middle joints need to be replaced.  The joint at the hood does not see the higher dp and should be fine.  It does not show any signs of collapsing.

I found four arms that had loose bolts on the hood supports at the end of the bottom tube.  I replace two bolts that were missing and tightened the other that were loose.

I had to adjust three arms for proper movement.  This is standard after arms have been in operation for some time.

The system operation is meeting all of their expectations (except for the flex problem).

Bill Boisvert

Bill Boisvert - Cell (919) 971-3910

Project Manager – Avani Environmental Intl.

E-mail bboisvert@avanienvironmental.com