January 28, 2008

Curtis Niagara LLC

50 Thielman Drive

Buffalo NY 14206-2364

Attention: Robert Filipski,

The following is a review of our meeting January 24 2008.

We reviewed the previous test results with the Dust Trak form March 2007. No changes have been made to any of the machines tested.

An Ambient count was as follows:T1 area 1.29 mg/m³ 										Assembly area .8 mg/m³

Production Office .192 mg/m³             Production area at door to Production Office 2.91 mg/m³

0.5 mg/m³ is the Time Waited Average that is acceptable in the USA.

The following chart shows the mg/m³ readings taken with the Dust Trak

| Machine # | Counts air cleaner ON March 2007 | Counts air cleaner ON Jan 2007 | Counts Air Cleaner OFF Jan. 2008 | Counts discharge of Air Cleaner | Counts Ambient at machine |
| --- | --- | --- | --- | --- | --- |
| 3308 500cfm | 33-39 | 3 to 5 | 40-45 | 2.99 | 2.90 |
| 3160 400cfm | 34-44 | OFF |  | 2.99 |  |
| 3170 400cfm | OFF | 3 to4 | 7 to 12 | 2.99 |  |
| 319 Acme 400cfm | 21-32 | 6 to 19 | 11 to 25 | 2.99 | 2.79 |
| 3309 400cfm | OFF | OFF |  | 2.99 |  |
| 3306 400cfm | 44-53 | OFF |  | 2.99 |  |
| 3718 |  | 100 plus |  | 1.57 |  |
| 356, 357 |  |  |  |  | 3.00 |
| 375 |  | 25 to 30 |  |  |  |
| 374 |  | 16 to 20 |  |  |  |
| 3712 |  | OFF |  |  |  |
| 3711 |  | OFF |  |  |  |
| 369 |  | OFF |  |  |  |
| 368 |  | OFF |  |  |  |
| 377 |  | OFF |  |  |  |

Using the efficiency calculator the discharge from the air cleaner for machines 3308/3160/3170/319/3309/3306 would be  5.98 mg/m³. This relates to 450lbs/year of mist filling the interior volume of the plant.

With Absolent the discharge will be .01 mg/m³ which will put 0.05984 lbs/year

This is the results of only one air cleaner servicing 6 machines.

Airborne oil is adding costs:

Exhaust Fans exhausting air at a cost of $1.68/cfm of air that is exhausted.

Housekeeping of Production and Main Office, production walls, floors, ceilings, machines etc.

Worker safety slippery floors and inhaling oil mists

Computer, calibrating / test equipment and other electrical items are being coated with oil reducing life cycle.

Savings

Oil collected in the Absolent units can be reused.

Filter life can last as long as 5 years from experience.  Analysis of current costs to maintain your equipment must be compared.

I look forward to working with you on this project.

Best Regards,

Bill Strouth.