Elgin Community College

Turn Over Report

November 9th, 2011

Avani Environmental Intl., Inc

95 Cypress Dr.

Youngsville, NC 27596

Submitted By:

William W. Boisvert

Project Manager

- September 7th and 8th.

  - Inspected motor that had short

    - Found that insufficient tape was used on motor terminations

    - Three terminations had short to the motor termination box cover.

    - Found that one of the three starter blocks that also failed due to the short.

      - Replaced bad starter

    - In checking out the motor found that three of the 12 motor leads had internal shorts.

    - Check start circuit and found that it worked properly.

    - Un-terminated the bad motor at the start panel, so that the one good motor on the collector could be used.

  - Inspected remaining three motor termination

    - Found bad taping and loose terminations in all three motors

    - Remover all tape, from all three motors

    - Tightened all terminations

    - Re-taped all terminations

  - Conducted training on, system operation

    - Proper Starting and Stopping of fans

    - Operation and adjustments of the pulse system

    - Filter removal and installation

    - Booth lighting and outs

  - Inspected all booths

    - Adjusted all slots on all booths

    - Adjusted all welding curtains

    - Inspected all lights – Sat.

- October 10th.

  - Remover bad motor

  - Installed new Motor/Fan assembly

  - Found that the new assemble would not work

    - Total assemble length to long

    - Fan wheel had interference with collector fan inlet nozzle

  - Left new fan in place to allow collector to be use as before

  - New Motor was never wired.

  - Crated original motor/fan assembly for return to our shop for motor rework

    - Rewind and testing

  - Found two pulse valves not seating properly

    - Disassembled valves

    - Found metal chips and cutting oil film in valves

      - This can only come from improper cleaning of the pipe at installation

    - Has able to get one of the two valves to operate correctly, one still has small air leakage.

- November 9th

  - Motor/ Fan Assembly

    - Removed Motor/Fan assembly

    - Installed reworked original motor/fan assembly

    - Made all motor terminations

    - Re-terminated leads at motor starters in Start/Stop panel.

    - Verified proper rotation.

    - Crated removed motor/fan for return to Avani

  - Pulse Valves

    - Found 2 valves leaking air

    - Found water, clips, misc. debris

    - Dissembled valves, cleaned both valves, reassembled valves, and reinstalled.

    - Both valves working satisfactory.

NOTE:  Air to pulse system need to be CLEAN and DRY.  Valves may need cleaning in the future.  This is not covered under the warranty.  Air system piping was not cleaned as it was installed or blown down prior to connection to our air receivers.

CUST0MER REMARKS: ________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________

Thanks,

Bill Boisvert

Bill Boisvert

Project Manager – Avani Environmental Intl.

Cell - 919-971-3910 / Office – 919-570-2861 X219

E-mail bboisvert@avanienvironmental.com