Customer:	Fleet Readiness Center

MCAS

Cherry Point, NC

Contact:	 Sarah Singleton

Phone: 		 252-464-7373

Email:		sarah.singleton@navy.mil

Date:  24 Jan. 2012

Project #:

Sales Order #: 16458

Serial #: 103501

Model #: SDC-5-4

AEI Crew:  Bill Boisvert

SCOPE OF PROJECT:        Installation – Service – (Warranty) – Demo – Delivery - Engineering

Collector # 1 was found to have a tripped starter overload.  I checked the amp draw on the motor and found it to be 6.1 to 6.3 amps.  The overload was set at 6 amps.  This caused the nuisance trip.  I checked at motors and reset all overloads. The amp reading for all fans are shown below.

| FAN | PHASE A (B) | PHASE B (O) | PHASE C (Y) |
| --- | --- | --- | --- |
| #1 | 6.1 | 6.3 | 6.3 |
| #2 | 6.0 | 6.2 | 6.1 |
| #3 | 5.8 | 6.1 | 6.1 |
| #4 | 6.0 | 6.2 | 6.2 |
| #5 | 5.8 | 6.0 | 6.1 |

All Overloads were set to 7.0 amps.

This should stop nuisance trips.

Thanks,

Bill Boisvert

Bill Boisvert - Cell (919) 971-3910

Project Manager – Avani Environmental Intl.

E-mail bboisvert@avanienvironmental.com

CUST0MER REMARKS: __________________________________________________________________________________________________________________________________________________________________ _________________________________________________________________________________

Customer Signature: _________________________________________Date:___________________

Title or Department: ________________________________________________________________