Gandi Unit Test Report

- Adjustments

  - Trip Current – Set to 1.5A

  - Reset Mode – Could Not Locate

  - Trip Class – Could Not Locate

- Hipot Test

  - Did not do – We do not have a Hipot Tester at this time

- Unit Test

  - Connect the Exhaust Unit to a power source – Completed

  - Turn on power source – Completed

  - Press the “Green” button – Done

  - Verify that the blower is Working – Sat

  - Press the Red” button – Done

  - Verify that the blower stops turning – Sat

  - Unlock and open the panel door – Done

  - Press the “Green” button – Done

  - Verify that the blower is Working – Sat

  - Press the “Red” Test button on the CEP7 relay – Done

  - Verify that the blower stops turning – Sat

  - Press the “Green” button – Done

  - Verify that the blower is Working – Sat

  - Rotate the “Trip” screw fully counter –clockwise – Done

  - Verify that the blower stops turning

  - Press the “Green” button – Done

  - Verify that the blower does not turn – Sat

  - Press the “Blue” Reset button – Done

  - Verify that the blower in working – Sat

  - Press the Red” button – Done

  - Verify that the blower stops turning – Sat

  - Close and lock the Panel Door. – Done

  - Turn off the temporary power supply – Done

  - Disconnect the Exhaust Unit from the power supply – Done

- Flow Test

  - Check air flow with bleed air damper shut and main air inlet damper full open.

  - Air Flow – 559 CFM

Test Completed By William W. Boisvert, IAQ Project Manager, 8/13/08