- OSKAR – AVANI ENVIRONMENTAL, INC.

- The Column Grid Arrangement for the SDC-30x2-40 Collector

is shown below:

Reference Drawing: #SV-5000-0225-01

COLUMN FOUNDATION ARRANGEMENT

SDC-30x2-40 SYSTEM

***

(+) Indicates Downward (Positive) Force (Y+)

(-) Indicates Upward (Negative) Force (Y-)

Loadings (MAX & MIN ONLY)

| Column |  | X (kips) | Load Case | Y (kips) | Load Case | Z (kips) | Load Case |
| --- | --- | --- | --- | --- | --- | --- | --- |
| R1A | max | 0.1 | 2 | 2.7 | 6 | 0.1 | 2 |
|  | min | -0.1 | 7 | 1.5 | 7 | -0.2 | 8 |
| R1B | max | 0.0 | 2 | 3.0 | 6 | 0.0 | 7 |
|  | min | -0.2 | 7 | 1.5 | 7 | -0.1 | 4 |
| R1C | max | 0.0 | 8 | 3.0 | 6 | 0.1 | 5 |
|  | min | -0.2 | 3 | 1.1 | 7 | -0.2 | 8 |
| R2A | max | -0.1 | 8 | 2.7 | 5 | 0.0 | 1 |
|  | min | -0.3 | 3 | 0.8 | 8 | -0.3 | 4 |
| R2B | max | 0.0 | 8 | 3.6 | 2 | 0.0 | 7 |
|  | min | -0.2 | 3 | 1.6 | 8 | -0.1 | 4 |
| R2C | max | 0.2 | 6 | 2.9 | 2 | 0.0 | 7 |
|  | min | 0.0 | 7 | 1.0 | 8 | -0.3 | 4 |

- Dead Load (LC 1)

| Column | X (kips) | Y (kips) | Z (kips) |
| --- | --- | --- | --- |
| R2B | 0.0 | 3.1 | 0.0 |
| R2C | 0.2 | 2.6 | 0.0 |
| R1B | 0.0 | 2.5 | 0.0 |
| R2A | -0.2 | 2.3 | 0.0 |
| R1C | -0.1 | 2.2 | 0.0 |
| R1A | 0.1 | 2.0 | 0.0 |
| Totals: | 0.0 | 14.7 | 0.0 |

Load Cases Used

| Load Cases |  | Factor |  | Factor |  | Factor |
| --- | --- | --- | --- | --- | --- | --- |
| 1: ASCE 1 (a) | DL | 1 |  |  |  |  |
| 2: ASCE 2 (a) | DL | 1 | LL | 1 |  |  |
| 3: ASCE 5 (b) (a) | DL | 1 | SX*SF | 0.7 |  |  |
| 4: ASCE 5 (b) (b) | DL | 1 | SZ*SF | 0.7 |  |  |
| 5: ASCE 6 (b) (a) | DL | 1 | SX*SF | 0.525 | LL | 0.75 |
| 6: ASCE 6 (b) (b) | DL | 1 | SZ*SF | 0.525 | LL | 0.75 |
| 7: ASCE 8 (a) | DL | 0.6 | SX*SF | 0.7 |  |  |
| 8: ASCE 8 (b) | DL | 0.6 | SZ*SF | 0.7 |  |  |

Note:

DL: Dead Load

LL: Live Load

SX: Seismic Load in X Direction

SZ: Seismic Load in Z Direction

*SF Denotes an internal Scaling Factor calculated by RISA.

**Seismic Loads calculated in accordance with ASCE 7-05 ASD (Section 2.4)

***Assumption: Site Classification D

- The maximum column compression loading is 3.6kips and occurs at column R2B.

- The maximum shear in the X direction is 0.3kips and occurs at column R2A.

- The maximum shear in the Z direction is 0.3kips and occurs at column R2A.

Note:

- These results are being provided based on the information provided and were generated using RISA-3-D Version 9.0.0 software program. Any certification of the reactions must be done by a certified Structural Engineer.