| Description | December 17, 2007 |
| --- | --- |

| Job Description: | Industrial Air Quality |  | Chicago Blower Sales - North Carolina |
| --- | --- | --- | --- |
| Reference: | Bob Venezia |  | David Redman |
| Fan Type: | Airfoil Centrifugal Fans |  | Phone: (704) 788-6893 |
| Fan Model: | Design 36A SQAD SW Direct Drive |  | Fax: (704) 788-7057 |
| Fan Size: | 18 1/4 |  | e-mail: cbsnc@vnet.net |
| Fan Width: | 100% |  |  |

| Performance |  |  |  |  |  | Values are in accordance with AMCA Standard 210 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Volume Flow Rate (CFM) | 7500 |
| --- | --- |
| Static Pressure (IN. WG) | 14 |
| Density (LB/FT³) | 0.075 |
| Temperature (°F) | 70 |
| Altitude (FT) | 0 |
| Speed (RPM) | 3442 |
| Power Required (BHP) | 23.3 |
| Static Efficiency (%) | 69.9 |
| Outlet Velocity (FT/MIN) | 3839 |
| Damper Opening (%) | N/A |

| Control Type |  | N/A |  |
| --- | --- | --- | --- |
| Outlet Area (FT²) | 1.95 |  |  |