## Head #1
Head #1 - CNC Cell #1 & #2
ODF-6000F SN:20071327
Gauge Readings - PA
Tower # | 1 | 2 | 3
1st Stage | 300 | 300 | 300
2nd Stage | 200 | 200 | 200
HEPA | 150 | 150 | 150
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.51 | 2860.1421 | 3991.4872 | 1 | 0.76 | 3491.4781 | 932.6368 | 1 | 0.54 | 2943.0619 | 786.145 | 1 |  | 0 | 0
2 | 0.47 | 2745.6897 | 3831.7625 | 2 | 0.67 | 3278.2338 | 875.6754 | 2 | 0.55 | 2970.1875 | 793.3907 | 2 |  | 0 | 0
3 | 0.45 | 2686.6357 | 3749.3493 | 3 | 0.59 | 3076.2989 | 821.735 | 3 | 0.49 | 2803.5 | 748.8655 | 3 |  | 0 | 0
4 | 0.46 | 2716.3232 | 3790.7799 | 4 | 0.58 | 3050.1171 | 814.7414 | 4 | 0.47 | 2745.6897 | 733.4233 | 4 |  | 0 | 0
5 | 0.45 | 2686.6357 | 3749.3493 | 5 | 0.49 | 2803.5 | 748.8655 | 5 | 0.53 | 2915.684 | 778.8318 | 5 |  | 0 | 0
6 | 0.42 | 2595.5366 | 3622.2156 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.46 | 2716.3232 | 3790.7799 | Average | 0.618 | 3148.4497 | 841.0078 | Average | 0.516 | 2876.9173 | 768.4765 | Average | 0 | 4500 | 1202.0312
Duct Area: | 1.3956 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712
Location # | TP5
Test Point | VP | V | CFM
1 | 0.45 | 2686.6357 | 717.6489
2 | 0.48 | 2774.7454 | 741.1846
3 | 0.47 | 2745.6897 | 733.4233
4 | 0.49 | 2803.5 | 748.8655
5 | 0.46 | 2716.3232 | 725.579
6 |  | 0 | 0
7 |  | 0 | 0
8 |  | 0 | 0
9 |  | 0 | 0
10 |  | 0 | 0
11 |  | 0 | 0
12 |  | 0 | 0
13 |  | 0 | 0
14 |  | 0 | 0
15 |  | 0 | 0
Average | 0.47 | 2745.6897 | 733.4233
Duct Area: | 0.26712
Length | Width | Area SF
0
Diameter
| 7 | 0.26712
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4 |  |  | Location # | TP5
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 |  | 0 | 0 | 1 | 0.65 | 3228.9342 | 862.5066 | 1 | 0.45 | 2686.6357 | 717.6489 | 1 |  | 0 | 0 | 1 | 0.44 | 2656.6165 | 709.6302
2 |  | 0 | 0 | 2 | 0.64 | 3204 | 855.8463 | 2 | 0.48 | 2774.7454 | 741.1846 | 2 |  | 0 | 0 | 2 | 0.47 | 2745.6897 | 733.4233
3 |  | 0 | 0 | 3 | 0.6 | 3102.2597 | 828.6696 | 3 | 0.47 | 2745.6897 | 733.4233 | 3 |  | 0 | 0 | 3 | 0.51 | 2860.1421 | 763.9956
4 |  | 0 | 0 | 4 | 0.59 | 3076.2989 | 821.735 | 4 | 0.48 | 2774.7454 | 741.1846 | 4 |  | 0 | 0 | 4 | 0.48 | 2774.7454 | 741.1846
5 |  | 0 | 0 | 5 | 0.62 | 3153.5402 | 842.3675 | 5 | 0.5 | 2831.9627 | 756.4684 | 5 |  | 0 | 0 | 5 | 0.45 | 2686.6357 | 717.6489
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0 | 0 | 0 | Average | 0.62 | 3153.5402 | 842.3675 | Average | 0.476 | 2763.1598 | 738.0899 | Average | 0 | 2580 | 689.1646 | Average | 0.47 | 2745.6897 | 733.4233
Duct Area: | 1.3956 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712 |  |  | Duct Area: | 0.26712
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712 |  |  | 7 | 0.26712

## Head #2
Head #2 - CNC Cell #3 & #4
ODF-6000F SN:20071325 &20071326
Gauge Readings - PA |  | (1325) |  | Gauge Readings - PA |  | (1326)
Tower # | 1 | 2 | 3 | Tower # | 1 | 2 | 3
1st Stage | 250 | 250 | 250 | 1st Stage | 250 | 250 | 250
2nd Stage | 200 | 200 | 200 | 2nd Stage | 200 | 200 | 200
HEPA | 150 | 150 | 150 | HEPA | 150 | 150 | 150
As Found
Location # | TP1A |  |  | Location # | TP1B |  |  | Location # | TP2 |  |  | Location # | TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.52 | 2888.0466 | 4030.4294 | 1 | 0.45 | 2686.6357 | 3749.3493 | 1 | 0.62 | 3153.5402 | 1100.2351 | 1 |  | 0 | 0
2 | 0.48 | 2774.7454 | 3872.3113 | 2 | 0.41 | 2564.4513 | 3578.8342 | 2 | 0.61 | 3128.005 | 1091.3262 | 2 |  | 0 | 0
3 | 0.42 | 2595.5366 | 3622.2156 | 3 | 0.41 | 2564.4513 | 3578.8342 | 3 | 0.62 | 3153.5402 | 1100.2351 | 3 |  | 0 | 0
4 | 0.39 | 2501.1217 | 3490.4543 | 4 | 0.39 | 2501.1217 | 3490.4543 | 4 | 0.58 | 3050.1171 | 1064.152 | 4 |  | 0 | 0
5 | 0.41 | 2564.4513 | 3578.8342 | 5 | 0.38 | 2468.8478 | 3445.4143 | 5 | 0.6 | 3102.2597 | 1082.3439 | 5 |  | 0 | 0
6 | 0.42 | 2595.5366 | 3622.2156 | 6 | 0.41 | 2564.4513 | 3578.8342 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.44 | 2656.6165 | 3707.4559 | Average | 0.40833 | 2559.2336 | 3571.5527 | Average | 0.606 | 3117.7324 | 1087.7422 | Average | 0 | 4200 | 1465.3333
Duct Area: | 1.3956 |  |  | Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
Location # | TP4 |  |  | Location # | TP5 |  |  | Location # | TP6 |  |  | Location # | TP7
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.47 | 2745.6897 | 957.9406 | 1 | 0.42 | 2595.5366 | 905.5539 | 1 |  | 0 | 0 | 1 | 0.47 | 2745.6897 | 957.9406
2 | 0.42 | 2595.5366 | 905.5539 | 2 | 0.41 | 2564.4513 | 894.7085 | 2 |  | 0 | 0 | 2 | 0.46 | 2716.3232 | 947.695
3 | 0.48 | 2774.7454 | 968.0778 | 3 | 0.39 | 2501.1217 | 872.6136 | 3 |  | 0 | 0 | 3 | 0.44 | 2656.6165 | 926.864
4 | 0.41 | 2564.4513 | 894.7085 | 4 | 0.41 | 2564.4513 | 894.7085 | 4 |  | 0 | 0 | 4 | 0.45 | 2686.6357 | 937.3373
5 | 0.42 | 2595.5366 | 905.5539 | 5 | 0.41 | 2564.4513 | 894.7085 | 5 |  | 0 | 0 | 5 | 0.44 | 2656.6165 | 926.864
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.44 | 2656.6165 | 926.864 | Average | 0.408 | 2558.1889 | 892.5237 | Average | 0 | 4700 | 1639.7778 | Average | 0.452 | 2692.5994 | 939.418
Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
Head #2 - CNC Cell #3 & #4
ODF-6000F SN:20071325 &20071326
AS Left
Location # | TP1A |  |  | Location # | TP1B |  |  | Location # | TP2 |  |  | Location # | TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.34 | 2335.2962 | 3259.0356 | 1 | 0.32 | 2265.5701 | 3161.729 | 1 | 0.47 | 2745.6897 | 957.9406 | 1 |  | 0 | 0
2 | 0.31 | 2229.8896 | 3111.9349 | 2 | 0.3 | 2193.6288 | 3061.3309 | 2 | 0.45 | 2686.6357 | 937.3373 | 2 |  | 0 | 0
3 | 0.31 | 2229.8896 | 3111.9349 | 3 | 0.28 | 2119.2468 | 2957.5266 | 3 | 0.42 | 2595.5366 | 905.5539 | 3 |  | 0 | 0
4 | 0.3 | 2193.6288 | 3061.3309 | 4 | 0.29 | 2156.7585 | 3009.8763 | 4 | 0.48 | 2774.7454 | 968.0778 | 4 |  | 0 | 0
5 | 0.29 | 2156.7585 | 3009.8763 | 5 | 0.31 | 2229.8896 | 3111.9349 | 5 | 0.44 | 2656.6165 | 926.864 | 5 |  | 0 | 0
6 | 0.29 | 2156.7585 | 3009.8763 | 6 | 0.3 | 2193.6288 | 3061.3309 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.30667 | 2217.8686 | 3095.1588 | Average | 0.3 | 2193.6288 | 3061.3309 | Average | 0.452 | 2692.5994 | 939.418 | Average | 0 | 2570 | 896.6444
Duct Area: | 1.3956 |  |  | Duct Area: | 1.3956 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 16 | 1.3956 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
Location # | TP4 |  |  | Location # | TP5 |  |  | Location # | TP6 |  |  | Location # | TP7
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.44 | 2656.6165 | 926.864 | 1 | 0.44 | 2656.6165 | 926.864 | 1 |  | 0 | 0 | 1 | 0.42 | 2595.5366 | 905.5539
2 | 0.43 | 2626.2541 | 916.2709 | 2 | 0.45 | 2686.6357 | 937.3373 | 2 |  | 0 | 0 | 2 | 0.41 | 2564.4513 | 894.7085
3 | 0.44 | 2656.6165 | 926.864 | 3 | 0.43 | 2626.2541 | 916.2709 | 3 |  | 0 | 0 | 3 | 0.43 | 2626.2541 | 916.2709
4 | 0.45 | 2686.6357 | 937.3373 | 4 | 0.42 | 2595.5366 | 905.5539 | 4 |  | 0 | 0 | 4 | 0.42 | 2595.5366 | 905.5539
5 | 0.42 | 2595.5366 | 905.5539 | 5 | 0.44 | 2656.6165 | 926.864 | 5 |  | 0 | 0 | 5 | 0.44 | 2656.6165 | 926.864
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.436 | 2644.5134 | 922.6413 | Average | 0.436 | 2644.5134 | 922.6413 | Average | 0 | 2540 | 886.1778 | Average | 0.424 | 2607.8671 | 909.8558
Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Head #3
Head #3 - Intermediate Wash
ODF-6000F SN:20071324
Gauge Readings - PA
Tower # | 1 | 2 | 3
1st Stage | 300 | 300 | 300
2nd Stage | 200 | 200 | 200
HEPA | 150 | 150 | 150
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.41 | 2564.4513 | 3578.8342 | 1 | 0.56 | 2997.0676 | 588.1745 | 1 | 0.89 | 3778.3094 | 2059.7034 | 1 | 0.24 | 1962.0413 | 1069.585
2 | 0.42 | 2595.5366 | 3622.2156 | 2 | 0.54 | 2943.0619 | 577.5759 | 2 | 0.9 | 3799.4766 | 2071.2425 | 2 | 0.22 | 1878.5115 | 1024.0497
3 | 0.39 | 2501.1217 | 3490.4543 | 3 | 0.58 | 3050.1171 | 598.5855 | 3 | 0.88 | 3757.023 | 2048.0994 | 3 | 0.2 | 1791.0904 | 976.3931
4 | 0.43 | 2626.2541 | 3665.0835 | 4 | 0.57 | 3023.7087 | 593.4028 | 4 | 0.87 | 3735.6153 | 2036.4292 | 4 | 0.19 | 1745.739 | 951.6702
5 | 0.43 | 2626.2541 | 3665.0835 | 5 | 0.55 | 2970.1875 | 582.8993 | 5 | 0.86 | 3714.0842 | 2024.6917 | 5 | 0.21 | 1835.3216 | 1000.5052
6 | 0.42 | 2595.5366 | 3622.2156 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.41667 | 2585.2164 | 3607.8131 | Average | 0.56 | 2997.0676 | 588.1745 | Average | 0.88 | 3757.023 | 2048.0994 | Average | 0.212 | 1844.0405 | 1005.2582
Duct Area: | 1.3956 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 6 | 0.19625 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514
Final Balance
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.43 | 2626.2541 | 3665.0835 | 1 | 0.45 | 2686.6357 | 527.2523 | 1 | 0.46 | 2716.3232 | 1480.7734 | 1 | 0.41 | 2564.4513 | 1397.9821
2 | 0.41 | 2564.4513 | 3578.8342 | 2 | 0.43 | 2626.2541 | 515.4024 | 2 | 0.46 | 2716.3232 | 1480.7734 | 2 | 0.42 | 2595.5366 | 1414.928
3 | 0.45 | 2686.6357 | 3749.3493 | 3 | 0.44 | 2656.6165 | 521.361 | 3 | 0.47 | 2745.6897 | 1496.7822 | 3 | 0.47 | 2745.6897 | 1496.7822
4 | 0.46 | 2716.3232 | 3790.7799 | 4 | 0.45 | 2686.6357 | 527.2523 | 4 | 0.44 | 2656.6165 | 1448.2249 | 4 | 0.43 | 2626.2541 | 1431.6733
5 | 0.45 | 2686.6357 | 3749.3493 | 5 | 0.43 | 2626.2541 | 515.4024 | 5 | 0.43 | 2626.2541 | 1431.6733 | 5 | 0.44 | 2656.6165 | 1448.2249
6 | 0.44 | 2656.6165 | 3707.4559 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.44 | 2656.6165 | 3707.4559 | Average | 0.44 | 2656.6165 | 521.361 | Average | 0.452 | 2692.5994 | 1467.8406 | Average | 0.434 | 2638.441 | 1438.3168
Duct Area: | 1.3956 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 6 | 0.19625 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514

## Head #4
Head #4 - GA Wash & GA Mill
ODF-4000TF SN:20071338
Gauge Readings - PA
1st Stage | 400
2nd Stage | 200
HEPA | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.53 | 2915.684 | 2288.8119 | 1 | 0.45 | 2686.6357 | 937.3373 | 1 | 0.59 | 3076.2989 | 1073.2865
2 | 0.54 | 2943.0619 | 2310.3036 | 2 | 0.46 | 2716.3232 | 947.695 | 2 | 0.57 | 3023.7087 | 1054.9384
3 | 0.49 | 2803.5 | 2200.7475 | 3 | 0.47 | 2745.6897 | 957.9406 | 3 | 0.54 | 2943.0619 | 1026.8016
4 | 0.48 | 2774.7454 | 2178.1751 | 4 | 0.45 | 2686.6357 | 937.3373 | 4 | 0.53 | 2915.684 | 1017.2498
5 | 0.5 | 2831.9627 | 2223.0907 | 5 | 0.44 | 2656.6165 | 926.864 | 5 | 0.55 | 2970.1875 | 1036.2654
6 | 0.51 | 2860.1421 | 2245.2115 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.50833 | 2855.4648 | 2241.5399 | Average | 0.454 | 2698.5499 | 941.4941 | Average | 0.556 | 2986.3446 | 1041.9024
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.53 | 2915.684 | 2288.8119 | 1 | 0.45 | 2686.6357 | 937.3373 | 1 | 0.59 | 3076.2989 | 1073.2865
2 | 0.54 | 2943.0619 | 2310.3036 | 2 | 0.46 | 2716.3232 | 947.695 | 2 | 0.57 | 3023.7087 | 1054.9384
3 | 0.49 | 2803.5 | 2200.7475 | 3 | 0.47 | 2745.6897 | 957.9406 | 3 | 0.54 | 2943.0619 | 1026.8016
4 | 0.48 | 2774.7454 | 2178.1751 | 4 | 0.45 | 2686.6357 | 937.3373 | 4 | 0.53 | 2915.684 | 1017.2498
5 | 0.5 | 2831.9627 | 2223.0907 | 5 | 0.44 | 2656.6165 | 926.864 | 5 | 0.55 | 2970.1875 | 1036.2654
6 | 0.51 | 2860.1421 | 2245.2115 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.50833 | 2855.4648 | 2241.5399 | Average | 0.454 | 2698.5499 | 941.4941 | Average | 0.556 | 2986.3446 | 1041.9024
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Head #5
Head #5 - Linebore
ODF-4000TF SN:20071320
Gauge Readings - PA
1st Stage | 300
2nd Stage | 200
HEPA | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.72 | 3398.3552 | 2667.7088 | 1 | 0.71 | 3374.673 | 1177.3859 | 1 | 0.29 | 2156.7585 | 752.4691 | 1 |  | 0 | 0
2 | 0.71 | 3374.673 | 2649.1183 | 2 | 0.68 | 3302.6076 | 1152.2431 | 2 | 0.3 | 2193.6288 | 765.3327 | 2 |  | 0 | 0
3 | 0.68 | 3302.6076 | 2592.547 | 3 | 0.74 | 3445.2313 | 1202.0029 | 3 | 0.28 | 2119.2468 | 739.3817 | 3 |  | 0 | 0
4 | 0.7 | 3350.8234 | 2630.3964 | 4 | 0.69 | 3326.8029 | 1160.6846 | 4 | 0.21 | 1835.3216 | 640.3233 | 4 |  | 0 | 0
5 | 0.71 | 3374.673 | 2649.1183 | 5 | 0.7 | 3350.8234 | 1169.0651 | 5 | 0.29 | 2156.7585 | 752.4691 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.704 | 3360.3835 | 2637.9011 | Average | 0.704 | 3360.3835 | 1172.4005 | Average | 0.274 | 2096.4176 | 731.4168 | Average | 0 | 5340 | 1863.0667
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.68 | 3302.6076 | 2592.547 | 1 | 0.63 | 3178.8702 | 1109.0725 | 1 | 0.6 | 3102.2597 | 1082.3439 | 1 |  | 0 | 0
2 | 0.7 | 3350.8234 | 2630.3964 | 2 | 0.62 | 3153.5402 | 1100.2351 | 2 | 0.59 | 3076.2989 | 1073.2865 | 2 |  | 0 | 0
3 | 0.77 | 3514.3732 | 2758.783 | 3 | 0.58 | 3050.1171 | 1064.152 | 3 | 0.61 | 3128.005 | 1091.3262 | 3 |  | 0 | 0
4 | 0.69 | 3326.8029 | 2611.5402 | 4 | 0.59 | 3076.2989 | 1073.2865 | 4 | 0.58 | 3050.1171 | 1064.152 | 4 |  | 0 | 0
5 | 0.72 | 3398.3552 | 2667.7088 | 5 | 0.54 | 2943.0619 | 1026.8016 | 5 | 0.57 | 3023.7087 | 1054.9384 | 5 |  | 0 | 0
6 | 0.68 | 3302.6076 | 2592.547 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.70667 | 3366.7419 | 2642.8924 | Average | 0.592 | 3081.5085 | 1075.1041 | Average | 0.59 | 3076.2989 | 1073.2865 | Average | 0 | 2520 | 879.2
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Head #6
Head #6 - Final Wash
ODF-6000F SN:20071323
Gauge Readings - PA
Tower # | 1 | 2 | 3
1st Stage | 400 | 350 | 350
2nd Stage | 200 | 200 | 200
HEPA | 200 | 200 | 200
As Found
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.46 | 2716.3232 | 3790.7799 | 1 | 0.85 | 3692.4276 | 724.6389 | 1 | 0.52 | 2888.0466 | 1574.3865 | 1 | 0.28 | 2119.2468 | 1155.2838
2 | 0.43 | 2626.2541 | 3665.0835 | 2 | 0.84 | 3670.6431 | 720.3637 | 2 | 0.48 | 2774.7454 | 1512.6216 | 2 | 0.29 | 2156.7585 | 1175.7329
3 | 0.44 | 2656.6165 | 3707.4559 | 3 | 0.9 | 3799.4766 | 745.6473 | 3 | 0.49 | 2803.5 | 1528.2969 | 3 | 0.32 | 2265.5701 | 1235.0504
4 | 0.46 | 2716.3232 | 3790.7799 | 4 | 0.88 | 3757.023 | 737.3158 | 4 | 0.5 | 2831.9627 | 1543.813 | 4 | 0.31 | 2229.8896 | 1215.5996
5 | 0.45 | 2686.6357 | 3749.3493 | 5 | 0.87 | 3735.6153 | 733.1145 | 5 | 0.51 | 2860.1421 | 1559.1747 | 5 | 0.3 | 2193.6288 | 1195.8324
6 | 0.44 | 2656.6165 | 3707.4559 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.44667 | 2676.6667 | 3735.4371 | Average | 0.868 | 3731.319 | 732.2714 | Average | 0.5 | 2831.9627 | 1543.813 | Average | 0.3 | 2193.6288 | 1195.8324
Duct Area: | 1.3956 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 6 | 0.19625 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514
As Left
Location # | TP1 |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.43 | 2626.2541 | 3665.0835 | 1 | 0.56 | 2997.0676 | 1633.8181 | 1 | 0.44 | 2656.6165 | 1448.2249 | 1 | 0.43 | 2626.2541 | 1431.6733
2 | 0.4 | 2532.9844 | 3534.9205 | 2 | 0.55 | 2970.1875 | 1619.1647 | 2 | 0.45 | 2686.6357 | 1464.5896 | 2 | 0.44 | 2656.6165 | 1448.2249
3 | 0.41 | 2564.4513 | 3578.8342 | 3 | 0.56 | 2997.0676 | 1633.8181 | 3 | 0.43 | 2626.2541 | 1431.6733 | 3 | 0.42 | 2595.5366 | 1414.928
4 | 0.39 | 2501.1217 | 3490.4543 | 4 | 0.57 | 3023.7087 | 1648.3412 | 4 | 0.42 | 2595.5366 | 1414.928 | 4 | 0.4 | 2532.9844 | 1380.8283
5 | 0.39 | 2501.1217 | 3490.4543 | 5 | 0.6 | 3102.2597 | 1691.1624 | 5 | 0.44 | 2656.6165 | 1448.2249 | 5 | 0.43 | 2626.2541 | 1431.6733
6 | 0.4 | 2532.9844 | 3534.9205 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.40333 | 2543.5166 | 3549.6187 | Average | 0.568 | 3018.3993 | 1645.4468 | Average | 0.436 | 2644.5134 | 1441.6271 | Average | 0.424 | 2607.8671 | 1421.6498
Duct Area: | 1.3956 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514 |  |  | Duct Area: | 0.54514
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514 |  |  | 10 | 0.54514

## Head #7
Head #7 - Henry System
ODF-4000TF SN:20071334 & 20071335
20071334 |  |  | 20071335
Gauge Readings - PA |  |  | Gauge Readings - PA
1st Stage | 300 |  | 1st Stage | 300
2nd Stage | 200 |  | 2nd Stage | 200
HEPA | 200 |  | HEPA | 200
As Found
Location # | TP1 |  |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4 |  |  | Location # | TP5
Test Point | VP | V | CFM |  | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.7 | 3350.8234 | 4676.2602 |  | 1 | 0.5 | 2831.9627 | 1250.4885 | 1 | 0.44 | 2656.6165 | 1173.0622 | 1 | 0.4 | 2532.9844 | 1118.4709 | 1 | 0.42 | 2595.5366 | 1146.0917
2 | 0.66 | 3253.6774 | 4540.6875 |  | 2 | 0.49 | 2803.5 | 1237.9205 | 2 | 0.46 | 2716.3232 | 1199.4264 | 2 | 0.42 | 2595.5366 | 1146.0917 | 2 | 0.42 | 2595.5366 | 1146.0917
3 | 0.59 | 3076.2989 | 4293.146 |  | 3 | 0.5 | 2831.9627 | 1250.4885 | 3 | 0.45 | 2686.6357 | 1186.3176 | 3 | 0.44 | 2656.6165 | 1173.0622 | 3 | 0.41 | 2564.4513 | 1132.3655
4 | 0.6 | 3102.2597 | 4329.3757 |  | 4 | 0.48 | 2774.7454 | 1225.2235 | 4 | 0.46 | 2716.3232 | 1199.4264 | 4 | 0.43 | 2626.2541 | 1159.6553 | 4 | 0.4 | 2532.9844 | 1118.4709
5 | 0.63 | 3178.8702 | 4436.29 |  | 5 | 0.46 | 2716.3232 | 1199.4264 | 5 | 0.45 | 2686.6357 | 1186.3176 | 5 | 0.44 | 2656.6165 | 1173.0622 | 5 | 0.43 | 2626.2541 | 1159.6553
6 | 0.62 | 3153.5402 | 4400.9405 |  | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 |  | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 |  | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 |  | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 |  | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 |  | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 |  | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 |  | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 |  | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 |  | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.63333 | 3187.2688 | 4448.0107 |  | Average | 0.486 | 2792.0337 | 1232.8574 | Average | 0.452 | 2692.5994 | 1188.9509 | Average | 0.426 | 2614.0105 | 1154.249 | Average | 0.416 | 2583.1474 | 1140.621
Duct Area: | 1.3956 |  |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156
Length | Width | Area SF |  |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  |  | 9 | 0.44156 |  |  | 9 | 0.44156 |  |  | 9 | 0.44156 |  |  | 9 | 0.44156
As Left
Location # | TP1 |  |  |  | Location # | TP2 |  |  | Location # | TP3 |  |  | Location # | TP4 |  |  | Location # | TP5
Test Point | VP | V | CFM |  | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.7 | 3350.8234 | 4676.2602 |  | 1 | 0.5 | 2831.9627 | 1250.4885 | 1 | 0.44 | 2656.6165 | 1173.0622 | 1 | 0.4 | 2532.9844 | 1118.4709 | 1 | 0.42 | 2595.5366 | 1146.0917
2 | 0.66 | 3253.6774 | 4540.6875 |  | 2 | 0.49 | 2803.5 | 1237.9205 | 2 | 0.46 | 2716.3232 | 1199.4264 | 2 | 0.42 | 2595.5366 | 1146.0917 | 2 | 0.42 | 2595.5366 | 1146.0917
3 | 0.59 | 3076.2989 | 4293.146 |  | 3 | 0.5 | 2831.9627 | 1250.4885 | 3 | 0.45 | 2686.6357 | 1186.3176 | 3 | 0.44 | 2656.6165 | 1173.0622 | 3 | 0.41 | 2564.4513 | 1132.3655
4 | 0.6 | 3102.2597 | 4329.3757 |  | 4 | 0.48 | 2774.7454 | 1225.2235 | 4 | 0.46 | 2716.3232 | 1199.4264 | 4 | 0.43 | 2626.2541 | 1159.6553 | 4 | 0.4 | 2532.9844 | 1118.4709
5 | 0.63 | 3178.8702 | 4436.29 |  | 5 | 0.46 | 2716.3232 | 1199.4264 | 5 | 0.45 | 2686.6357 | 1186.3176 | 5 | 0.44 | 2656.6165 | 1173.0622 | 5 | 0.43 | 2626.2541 | 1159.6553
6 | 0.62 | 3153.5402 | 4400.9405 |  | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 |  | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 |  | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 |  | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 |  | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 |  | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 |  | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 |  | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 |  | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 |  | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.63333 | 3187.2688 | 4448.0107 |  | Average | 0.486 | 2792.0337 | 1232.8574 | Average | 0.452 | 2692.5994 | 1188.9509 | Average | 0.426 | 2614.0105 | 1154.249 | Average | 0.416 | 2583.1474 | 1140.621
Duct Area: | 1.3956 |  |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156
Length | Width | Area SF |  |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 16 | 1.3956 |  |  |  | 9 | 0.44156 |  |  | 9 | 0.44156 |  |  | 9 | 0.44156 |  |  | 9 | 0.44156

## Head #8
Head #8 - MTS Collector
ODF-2000T SN:20071340
Gauge Readings - PA
1st Stage | 200
2nd Stage | 200
HEPA | 200
As Found |  |  |  | As Left
Location # | TP1 |  |  | Location # | TP1
Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.5 | 2831.9627 | 988.0403 | 1 | 0.5 | 2831.9627 | 988.0403
2 | 0.49 | 2803.5 | 978.11 | 2 | 0.49 | 2803.5 | 978.11
3 | 0.49 | 2803.5 | 978.11 | 3 | 0.49 | 2803.5 | 978.11
4 | 0.52 | 2888.0466 | 1007.6074 | 4 | 0.52 | 2888.0466 | 1007.6074
5 | 0.55 | 2970.1875 | 1036.2654 | 5 | 0.55 | 2970.1875 | 1036.2654
6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.51 | 2860.1421 | 997.8718 | Average | 0.51 | 2860.1421 | 997.8718
Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter
| 8 | 0.34889 |  |  | 8 | 0.34889