- Dahlonega Plant Equipment Standards

- 23/01MAY2003

- APPROVED BY:  H.DAVIS / R. ADAMS

These standards are for use in the Dahlonega plant during construction and equipment purchase.  Any exceptions must be submitted to Plant Services for approval in writing.  These standards are maintained in the plant services files.

WIRING		Color Code

480 Volt  Black with Green Ground

277 volt Black with White Neutral

240 volt  Red with Green Ground

120 Volt Red with White Neutral and Green Ground

Ac Control Voltages  Red with White Neutral

Dc Control Voltages  Blue 14 Gage Min.

Wiring Stranded M.T.W. ( Machine Tool Wired I.A.W.)

All Wiring To Be Numbered And Documented On Electrical Print

Wires To Be Tied And Wire Ways Used

Terminal Strip  Allen Bradley C Series

Conduit  Rigid  Galvanized Unless In Atmospheres That Are Not Compatible With Galvanized

Outlets  120 Volt Min. Of 20 Amp Rating With Gfi

All Devices To Grounded With Wiring Not Through Conduit  Ground Wire Green 14 Gage Min.

Natural Gas	Natural Gas line pressure for the plant is 5psi.

Wire Way	G-4000 Series

Panels		Hoffman Nema 12  Min. Oil And Water Tight  No Door Mount Disconnects For Main Breaker 					Flange Mount Disconnects, Lighting Package For Panels Taller That 45"

Breaker And Distribution Panels To Be Sq.D I-Line Series With Sq.D Breakers

Starters		Furnas Sp100 With Electronic Trips

MCC		Furnas  (Motor Control Center)

Switches	Cutler Hammer  30.5 Mm Size Operators	 Glass Lens Only No Plastic

Each panel should include a Mushroom Emergency Stop.

Limit Switch	Cutler Hammer

PLC		MODICON - MOMENTUM OR QUANTUM    Using concept software Ver. 2.0. Alternatives include

IDEC  FA2 or FA3.  Any exception to be approved by maintenance.

Transformers	480 To 120/240 Sq. D.  No 208 Voltages

Bearings	Torrington Or Fafnir Any Exceptions In Writing With Cross Over Reference Numbers

Soft Starts	Nordic

Vfd's		Magnetek  Gpd Series

Motors		Baldor  Premium Energy Efficient Rating 1.5 Min. Service Factor, Washdown Proof

All motors shall be specified and tested in accordance with NEMA Standard MG-1Part 12, IEEE Test

Procedure 112, Method B.  The minimum efficiency shall be guaranteed.

Pneumatics	Aro Products, No Plastic Regulator Or Filter Bowls, Glass With Guards

Pumps		Electric; 	Gusher, I-R ( IDP ), Flygt

Air;  Aro,  Wilden

Gauges		Liquid Filled

Piping		Valves 300# Rating  Pvc Schedule 80 Min. Air Lines In Galvanized,

Natural Gas Valves To Be Cocks Only No Ball Valves

Lube		Mobil Products (With MSDS Supplied)

Prints		3 Sets Required Including Electrical, Pneumatic, Mechanical, Operator Manual ,Parts Listing

Recommended Spares, Suggested Manufacturer P.M. Checks

Recommended Vibration Specs,  All Prints Autocad Dxf Format On Disk

Chemicals	Must Pass The Corporate Plant Engineering Guide Lines Chemical Selection 8-1-94

MSDS Required Prior To Receipt Of Any Chemical And Plant Services Approval	,

In Returnable Containers No Non-Returnable Containers

Vendor to supply drum management if drums required.

Paper 		Recycled Used Where Possible

Door		Locks, Operators Schlage With Current Locking System

Hardware	Closures   LCN     Exit Devices  Von Duprin

Glynn-Johnson  Door Holders.  Mascotech Steelcraft  Doors.

Floor Coatings	Garland Floor Coating Systems

Aisles		Green  		With Yellow Outline For Safety

Work Areas	Dark Gray 	Garland Floor Coating Systems

Guarding	Must Meet Osha Requirements For Pinch Points, Guarding,

Ergonomics 	Review By Task Team,

- Plant Color Coding For Piping, Etc.

All lines for the delivery of air, water, waste , natural gas etc. Will be color coded and labeled according to the following standards.  If lines are insulated the outer wrap will also be color coded as will the initial piping to assure knowledge of the color code.  These color codes are use to assure knowledge of materials contained in piping.  Labeling will be Seton Co.  Labeling will occur at least once every 50 feet and on every drop with arrows showing the direction of flow from the source.  Galvanized or copper lines are to be labeled only. Lines containing liquid in temperatures greater than 1200f will be insulated.  Insulation colors will be matching to pipe color.

LINE TYPE				LABEL		LABEL		PIPE 		PAINT

COLOR		REQ'D		COLOR		(GLIDDEN)

POTABLE WATER			GREEN		YES		GREEN		SAFETY GREEN

CHILLED  WATER RETURN		GREEN		YES		GREEN		MED. GREEN

CHILLED WATER SUPPLY		GREEN		YES		GREEN		SUPPORT GREEN

NATURAL GAS				YELLOW	YES		YELLOW	SAFETY YELLOW

PROPANE				YELLOW	YES		YELLOW	CAT YELLOW

GRIND COOLANTS			GRAY		YES		NONE

COMPRESSED AIR			BLUE		YES		BLUE		SAFETY BLUE

WASTE LINES				GREEN		YES		NONE

TREATED WASTE			BLUE		YES		WHITE		COMMERCIAL WHITE

ROOF DRAINS				GREEN		NO		NONE

METHANOL				YELLOW	YES		BROWN

SULFURIC ACID 			YELLOW	YES		SS LINES@

QUENCH OILS				YELLOW	YES		BLACK		BLACK

USED OILS				YELLOW	YES		BLACK		BLACK

FIRE PROTECTION LINES		RED		YES		RED		SAFETY RED

RUST INHIBITOR			GREEN		YES		GRAY		SERVICE GRAY

DIESEL					YELLOW	YES		ORANGE	SAFETY ORANGE

POLYMER LINES			GREEN		YES		GRAY		SAFETY GRAY

DEFOAMER				YELLOW	YES		GRAY		SAFETY GRAY

Floor in front of safety equipment will be marked with a yellow square to maintain clearance to equipment. Equipment to be marked

includes fire extinguishers, fire hoses and eye wash stations. This requirement applies to the manufacturing areas of the plant, or to

other areas as required. A stripe will be marked on the wall behind the piece of safety equipment up to 2 blocks wide with the

following colors.

Fire equipment ( hoses and extinguishers )  Red

Stretchers and eye wash                             Green

Hot Sticks                                                    Yellow

* BASED ON ANSI  A13.-1981 STD. SCHEME OF PIPING IDENTIFICATION

@ if insulated use yellow outer cover.

- Year 2000 Compliance

All equipment  must be year 2000 compliance. This must be confirmed with written certification, or within the Quote.

- CONTRACTOR REQUIREMENTS

- INSURANCE

Insurance certificates must be on file with purchasing.  Liability requirements must meet a minimum of $500,000.  It is preferred that contractors have a drug and alcohol screening process.

- POWERED VEHICLE USE

Lift Truck, Sky lifts, or other power fork truck operators must complete an approved training program.  License must be displayed by operator and on file.

Contractor is expected to provide all lift trucks, or lifts to be used during project.  Any exception must be approved by the Maintenance Manager prior to purchase order agreements.

- SAFETY TRAINING

Prior to starting a job all individuals who will be on site are required to complete Safety Training.  Safety Training is provided by Facilities Technician.

All individuals while on site are expected to follow all safety rules and guidelines established by Torrington or OSHA.

Any chemicals to be used on site must have MSDS reviewed by Facilities Technician prior to introduction to the site.

- MACHINED COMPONENTS INSPECTION

All projects that consist of machined components for repair or build are expected to be inspected per plant inspection procedure.  43-0630004, 43-060005

- AIR CONSUMPTION

All air lines to be equipped with regulators.  Air consumption to be minimized.  All air devices to operate on 80 psi.