## TC Case
Location #: | 1323-TP1
Test Point | VP | V | CFM
1 | 0.63 | 3178.8702 | 1109.0725 | Filter Reading
2 | 0.6 | 3102.2597 | 1082.3439 | HEPA | 200 Pa
3 | 0.59 | 3076.2989 | 1073.2865 | 2nd stage | 200 Pa
4 | 0.61 | 3128.005 | 1091.3262 | 1st stage | 300 Pa
5 | 0.62 | 3153.5402 | 1100.2351
6 |  | 0 | 0
Average | 0.61 | 3128.005 | 1091.3262
Duct Area: | 0.34889
Length | Width | Area SF
0
Diameter
| 8 | 0.34889
Location #: | 1326-TP1 |  |  | Location #: | 1326-TP2 |  |  | Location #: | 1326-TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Filter Reading
1 | 0.65 | 3228.9342 | 2534.7134 | 1 | 1.46 | 4839.2599 | 2136.8357 | 1 | 1.25 | 4477.7261 | 1977.1959 | HEPA | 200 Pa
2 | 0.62 | 3153.5402 | 2475.529 | 2 | 0.2 | 1791.0904 | 790.8784 | 2 | 0.34 | 2335.2962 | 1031.1792 | 2nd stage | 200 Pa
3 | 0.63 | 3178.8702 | 2495.4131 | 3 | 0.12 | 1387.3727 | 612.6118 | 3 | 0.22 | 1878.5115 | 829.4802 | 1st stage | 300 Pa
4 | 0.55 | 2970.1875 | 2331.5972 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.54 | 2943.0619 | 2310.3036 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.598 | 3097.0849 | 2431.2117 | Average | 0.59333 | 3084.9767 | 1362.21 | Average | 0.60333 | 3110.8651 | 1373.6414
Duct Area: | 0.785 |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 9 | 0.44156 |  |  | 9 | 0.44156
Location #: | 1608-TP1 |  |  | Location #: | 1608-TP2 |  |  | Location #: | 1608-TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | Filter Reading
1 | 0.36 | 2403 | 2567.5388 | 1 | 1.42 | 4772.5083 | 2107.3607 | 1 | 1.18 | 4350.5436 | 1921.0369 |  | 1st Tower | 2nd Tower | 3rd Tower
2 | 0.43 | 2626.2541 | 2806.0796 | 2 | 0.54 | 2943.0619 | 1299.5458 | 2 | 0.33 | 2300.6973 | 1015.9017 | HEPA | 100 Pa | 100 Pa | 100 Pa
3 | 0.43 | 2626.2541 | 2806.0796 | 3 | 0.22 | 1878.5115 | 829.4802 | 3 | 0.36 | 2403 | 1061.0747 | 2nd stage | 100 Pa | 100 Pa | 100 Pa
4 | 0.47 | 2745.6897 | 2933.6931 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 1st stage | 200 Pa | 200 Pa | 200 Pa
5 | 0.45 | 2686.6357 | 2870.5956 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.428 | 2620.1394 | 2799.5462 | Average | 0.72667 | 3414.0521 | 1507.5174 | Average | 0.62333 | 3162.006 | 1396.2233
Duct Area: | 1.0685 |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 14 | 1.0685 |  |  | 9 | 0.44156 |  |  | 9 | 0.44156
Location #: | 1607-TP1 |  |  | Location #: | 1607-TP2 |  |  | Location #: | 1607-TP3 |  |  | Location #: | 1607-TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | Filter Reading
1 | 0.59 | 3076.2989 | 3286.9399 | 1 | 1.74 | 5282.9578 | 2332.7561 | 1 | 1.59 | 5050.1128 | 2229.9405 | 1 | 1.63 | 5113.2417 | 2257.8158 |  | 1st Tower | 2nd Tower | 3rd Tower
2 | 0.55 | 2970.1875 | 3173.5628 | 2 | 0.21 | 1835.3216 | 810.4092 | 2 | 0.16 | 1602 | 707.3831 | 2 | 0.19 | 1745.739 | 770.8529 | HEPA | 100 Pa | 100 Pa | 100 Pa
3 | 0.54 | 2943.0619 | 3144.5799 | 3 | 0.18 | 1699.1776 | 750.2931 | 3 | 0.12 | 1387.3727 | 612.6118 | 3 | 0.15 | 1551.1298 | 684.9208 | 2nd stage | 100 Pa | 100 Pa | 100 Pa
4 | 0.55 | 2970.1875 | 3173.5628 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 1st stage | 200 Pa | 200 Pa | 200 Pa
5 | 0.59 | 3076.2989 | 3286.9399 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.564 | 3007.7523 | 3213.6998 | Average | 0.71 | 3374.673 | 1490.129 | Average | 0.62333 | 3162.006 | 1396.2233 | Average | 0.65667 | 3245.4506 | 1433.0693
Duct Area: | 1.0685 |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156 |  |  | Duct Area: | 0.44156
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 14 | 1.0685 |  |  | 9 | 0.44156 |  |  | 9 | 0.44156 |  |  | 9 | 0.44156

## M Case
Location #: | 1328-TP1 |  |  | Location #: | 1328-TP2 |  |  | Location #: | 1328-TP3 |  |  | Location #: | 1328-TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | 1328 | Filter Reading
1 | 0.52 | 2888.0466 | 3085.7975 | 1 | 1.48 | 4872.2928 | 1699.8888 | 1 | 1.41 | 4755.674 | 1659.2018 | 1 | 1.46 | 4839.2599 | 1688.364 |  | 1st Tower | 2nd Tower | 3rd Tower
2 | 0.48 | 2774.7454 | 2964.7384 | 2 | 0.15 | 1551.1298 | 541.172 | 2 | 0.34 | 2335.2962 | 814.7589 | 2 | 0.06 | 981.0206 | 342.2672 | HEPA | 100 Pa | 100 Pa | 100 Pa
3 | 0.58 | 3050.1171 | 3258.9654 | 3 | 0.17 | 1651.3038 | 576.1215 | 3 | 0.29 | 2156.7585 | 752.4691 | 3 | 0.08 | 1132.7851 | 395.2161 | 2nd stage | 100 Pa | 100 Pa | 100 Pa
4 | 0.59 | 3076.2989 | 3286.9399 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 1st stage | 200 Pa | 200 Pa | 200 Pa
5 | 0.59 | 3076.2989 | 3286.9399 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.552 | 2975.5829 | 3179.3277 | Average | 0.6 | 3102.2597 | 1082.3439 | Average | 0.68 | 3302.6076 | 1152.2431 | Average | 0.53333 | 2924.8385 | 1020.4436
Duct Area: | 1.0685 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | 1329 | Filter Reading
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  | 1st Tower | 2nd Tower | 3rd Tower
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  | HEPA | 100 Pa | 100 Pa | 100 Pa
| 14 | 1.0685 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  | 2nd stage | 100 Pa | 100 Pa | 100 Pa
[16 empty] | 1st stage | 200 Pa | 200 Pa | 200 Pa
Location #: | 1329 -TP1 |  |  | Location #: | 1329 -TP2 |  |  | Location #: | 1329 -TP3 |  |  | Location #: | 1329 -TP4 |  |  | Location #: | 1329 -TP5
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.8 | 3582.1809 | 3827.4608 | 1 | 1.23 | 4441.7599 | 1549.6807 | 1 | 1.08 | 4162.1181 | 1452.1168 | 1 | 1.09 | 4181.3428 | 1458.824 | 1 | 1.06 | 4123.3999 | 1438.6084
2 | 0.86 | 3714.0842 | 3968.3958 | 2 | 0.19 | 1745.739 | 609.0689 | 2 | 0.25 | 2002.5 | 698.65 | 2 | 0.24 | 1962.0413 | 684.5344 | 2 | 0.39 | 2501.1217 | 872.6136
3 | 0.84 | 3670.6431 | 3921.9802 | 3 | 0.25 | 2002.5 | 698.65 | 3 | 0.26 | 2042.1573 | 712.486 | 3 | 0.24 | 1962.0413 | 684.5344 | 3 | 0.21 | 1835.3216 | 640.3233
4 | 0.78 | 3537.1202 | 3779.3147 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.88 | 3757.023 | 4014.2747 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.832 | 3653.1221 | 3903.2594 | Average | 0.55667 | 2988.1344 | 1042.5269 | Average | 0.53 | 2915.684 | 1017.2498 | Average | 0.52333 | 2897.2883 | 1010.8317 | Average | 0.55333 | 2979.1745 | 1039.4009
Duct Area: | 1.0685 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 14 | 1.0685 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
Location #: | 1327-TP1 |  |  | Location #: | 1327-TP2 |  |  | Location #: | 1327-TP3 |  |  | Location #: | 1327-TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Filter Reading
1 | 0.8 | 3582.1809 | 2812.012 | 1 | 1.44 | 4806 | 1676.76 | 1 | 1.35 | 4653.3895 | 1623.5159 | 1 | 1.29 | 4548.8056 | 1587.0277 | HEPA | 200 Pa
2 | 0.82 | 3626.6817 | 2846.9452 | 2 | 0.19 | 1745.739 | 609.0689 | 2 | 0.29 | 2156.7585 | 752.4691 | 2 | 0.31 | 2229.8896 | 777.9837 | 2nd stage | 200 Pa
3 | 0.87 | 3735.6153 | 2932.458 | 3 | 0.2 | 1791.0904 | 624.8916 | 3 | 0.24 | 1962.0413 | 684.5344 | 3 | 0.28 | 2119.2468 | 739.3817 | 1st stage | 400 Pa
4 | 0.88 | 3757.023 | 2949.2631 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.79 | 3559.7219 | 2794.3817 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.832 | 3653.1221 | 2867.7008 | Average | 0.61 | 3128.005 | 1091.3262 | Average | 0.62667 | 3170.4493 | 1106.1345 | Average | 0.62667 | 3170.4493 | 1106.1345
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889

## Valve Body
Location #: | 1349-TP1
Test Point | VP | V | CFM | Filter Reading
1 | 0.62 | 3153.5402 | 1100.2351 | HEPA
2 | 0.65 | 3228.9342 | 1126.5393 | 2nd stage
3 | 0.66 | 3253.6774 | 1135.1719 | 1st stage
4 | 0.72 | 3398.3552 | 1185.6484
5 | 0.64 | 3204 | 1117.84
6 |  | 0 | 0
Average | 0.658 | 3248.7438 | 1133.4506
Duct Area: | 0.34889
Length | Width | Area SF
0
Diameter
| 8 | 0.34889
Location #: | 1610-TP1 |  |  | Location #: | 1610-TP2 |  |  | Location #: | 1610-TP3 |  |  | Location #: | 1610-TP4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | Filter Reading
1 | 0.54 | 2943.0619 | 3144.5799 | 1 | 0.38 | 2468.8478 | 484.5114 | 1 | 0.98 | 3964.7477 | 2615.2192 | 1 | 0.87 | 3735.6153 | 733.1145 |  | 1st Tower | 2nd Tower | 3rd Tower
2 | 0.43 | 2626.2541 | 2806.0796 | 2 | 0.42 | 2595.5366 | 509.3741 | 2 | 0.76 | 3491.4781 | 2303.042 | 2 | 0.97 | 3944.4675 | 774.1018 | HEPA | 100 | 100 | 100
3 | 0.42 | 2595.5366 | 2773.2588 | 3 | 0.43 | 2626.2541 | 515.4024 | 3 | 0.95 | 3903.5911 | 2574.8792 | 3 | 0.72 | 3398.3552 | 666.9272 | 2nd stage | 100 | 100 | 100
4 | 0.43 | 2626.2541 | 2806.0796 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 1st stage | 200 | 200 | 200
5 | 0.49 | 2803.5 | 2995.4619 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.462 | 2722.2218 | 2908.6184 | Average | 0.41 | 2564.4513 | 503.2736 | Average | 0.89667 | 3792.434 | 2501.558 | Average | 0.85333 | 3699.6605 | 726.0584
Duct Area: | 1.0685 |  |  | Duct Area: | 0.19625 |  |  | Duct Area: | 0.65962 |  |  | Duct Area: | 0.19625
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 14 | 1.0685 |  |  | 6 | 0.19625 |  |  | 11 | 0.65962 |  |  | 6 | 0.19625
Location #: | 1604-TP1 |  |  | Location #: | 1604-TP2 |  |  | Location #: | 1604-TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Filter Reading
1 | 0.66 | 3253.6774 | 2554.1367 | 1 | 2.87 | 6784.9003 | 2367.1763 | 1 |  | 0 | 0 | HEPA | 200
2 | 0.72 | 3398.3552 | 2667.7088 | 2 | 2.6 | 6457.8685 | 2253.0786 | 2 |  | 0 | 0 | 2nd stage | 200
3 | 0.72 | 3398.3552 | 2667.7088 | 3 | 2.71 | 6593.0621 | 2300.2461 | 3 |  | 0 | 0 | 1st stage | 200
4 | 0.73 | 3421.8735 | 2686.1707 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.81 | 3604.5 | 2829.5325 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.728 | 3417.1828 | 2682.4885 | Average | 2.7267 | 6613.3049 | 2307.3086 | Average | 0 | 0 | 0
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
Location #: | 1603-TP1 |  |  | Location #: | 1603-TP2 |  |  | Location #: | 1603-TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Filter Reading
1 | 0.56 | 2997.0676 | 2352.698 | 1 | 2.06 | 5748.2564 | 2005.5028 | 1 | 1.77 | 5328.3059 | 1858.9867 | HEPA | 100
2 | 0.54 | 2943.0619 | 2310.3036 | 2 | 0.11 | 1328.3082 | 463.432 | 2 | 0.71 | 3374.673 | 1177.3859 | 2nd stage | 100
3 | 0.57 | 3023.7087 | 2373.6113 | 3 | 0.46 | 2716.3232 | 947.695 | 3 | 0.26 | 2042.1573 | 712.486 | 1st stage | 200
4 | 0.55 | 2970.1875 | 2331.5972 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.67 | 3278.2338 | 2573.4135 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.578 | 3044.8538 | 2390.2102 | Average | 0.87667 | 3749.9007 | 1308.2987 | Average | 0.91333 | 3827.5174 | 1335.3783
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889
Location #: | 1609-TP1 |  |  | Location #:
Test Point | VP | V | CFM | Test Point | VP | V | CFM |  | Filter Reading
1 | 0.41 | 2564.4513 | 2740.0449 | 1 |  | 0 | 0 |  | 1st Tower | 2nd Tower | 3rd Tower
2 | 0.39 | 2501.1217 | 2672.3791 | 2 |  | 0 | 0 | HEPA | 100 | 100 | 100
3 | 0.34 | 2335.2962 | 2495.1992 | 3 |  | 0 | 0 | 2nd stage | 100 | 100 | 100
4 | 0.38 | 2468.8478 | 2637.8953 | 4 |  | 0 | 0 | 1st stage | 100 | 100 | 100
5 | 0.29 | 2156.7585 | 2304.4366 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.362 | 2409.6658 | 2574.6609 | Average | 0 | 0 | 0
Duct Area: | 1.0685 |  |  | Duct Area: | 0.19625
Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter
| 14 | 1.0685 |  |  | 6 | 0.19625
Location #: | 1602-TP1
Test Point | VP | V | CFM | Filter Reading
1 | 0.13 | 1444.0233 | 1542.8988 | HEPA | 100
2 | 0.12 | 1387.3727 | 1482.3692 | 2nd stage | 100
3 | 0.15 | 1551.1298 | 1657.3391 | 1st stage | 100
4 | 0.13 | 1444.0233 | 1542.8988
5 | 0.18 | 1699.1776 | 1815.5241
6 |  | 0 | 0
Average | 0.142 | 1509.1996 | 1612.5379
Duct Area: | 1.0685
Length | Width | Area SF
0
Diameter
| 14 | 1.0685
Location #: | 1324-TP1 |  |  | Location #: | 1324-TP2 |  |  | Location #: | 1324-TP3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Filter Reading
1 | 0.42 | 2595.5366 | 2037.4963 | 1 | 0.69 | 3326.8029 | 1160.6846 | 1 |  | 0 | 0 | HEPA | 200
2 | 0.42 | 2595.5366 | 2037.4963 | 2 | 0.65 | 3228.9342 | 1126.5393 | 2 |  | 0 | 0 | 2nd stage | 200
3 | 0.44 | 2656.6165 | 2085.4439 | 3 | 0.39 | 2501.1217 | 872.6136 | 3 |  | 0 | 0 | 1st stage | 200
4 | 0.45 | 2686.6357 | 2109.009 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 | 0.54 | 2943.0619 | 2310.3036 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
Average | 0.454 | 2698.5499 | 2118.3616 | Average | 0.57667 | 3041.3398 | 1061.0897 | Average | 0 | 0 | 0
Duct Area: | 0.785 |  |  | Duct Area: | 0.34889 |  |  | Duct Area: | 0.34889
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 12 | 0.785 |  |  | 8 | 0.34889 |  |  | 8 | 0.34889