Date: 	8/25/09	       Project#:  	Unit Inspection	IAQ Crew:  Bill B. & Jim J.

Customer:	Honeywell					Installation:

Duncan, SC					Service: X

Scott Lorick					Warranty:

Repair:

# Scope Of Project

- Header # 2

  - SN: 20050158

  - Checked gauges and lines – Sat.

  - Checked pump and float operation – Sat.

  - Gauge reading taken:

    - 1st Stage – 200PA

    - 2nd Stage – 400PA

    - HEPA – 2000PA

  - HEPA Filter needs to be changed ASAP, filters over 2000PA can self destruct.

- Header # 4

  - SN:20050160

  - Checked gauges and lines – Sat.

  - Checked pump and float operation – Sat.

  - Gauge reading taken:

    - 1st Stage – 200PA

    - 2nd Stage – 200PA

    - HEPA – 100PA

- Header #6

  - 20050159

  - Gauges appear to be OK

  - Gauges line have oil and need to be completely replaced

  - Checked pump and float operation – Sat.

  - No Gauge readings available

- Header #7

  - SN:2005150

  - Checked gauges and lines – Sat.

  - Checked pump and float operation – Sat.

    - Oil Pump sump appears to have a sludge build up, this build up is affecting pump automatic operation.

    - Entire unit sump area needs to be cleaned.

  - Gauge reading taken:

    - 1st Stage – 600PA

    - 2nd Stage – 400PA

    - HEPA – 1400PA

  - HEPA Filter needs to be changed soon

- Header #9

  - No Serial Number

  - No HEPA filter installed

  - 1st stage gauge found to be below zero when gauge line removed.

  - Gauge reading of follows;

    - 1st stage – 500PA

    - 2nd stage – 200PA

  - Checked pump and float operation – Sat.

- Header #10

  - SN: 20030584

  - No HEPA filter installed

  - Checked gauges and lines – Sat.

  - Gauge reading of follows;

    - 1st stage – 1200PA

    - 2nd stage – 400PA

  - Checked pump and float operation – Sat.

- Header #11

  - No Serial Number

  - No HEPA filter installed

  - Float assembly bad, contacts sticking

  - Checked gauges and lines – Sat.

  - Gauge reading of follows;

    - 1st stage – 1200PA

    - 2nd stage – 400PA

  - Pump operates sat.

Units with no HEPA filters need to have them install soon.  The units with float operation issues can be dealt with latter.  Units with gauge problems  are less of a problem.

Inspection completed by:

Bill Boisvert, Project Manager, Industrial Air Quality

Office Phone – 919-562-7181 X219

Cell – 919-971-3910

CUSTOMER REMARKS:

CUSTOMER SIGNATURE:						DATE:

TITLE OR DEPARTMENT: