## Sheet1
V=4005{(SQTR)VP}
VP | V | VP | V | VP | V | VP | V | VP | V | VP | V | VP | V | VP | V | VP | V | VP | V | VP | V | VP | V | VP | V
0.01 | 400.5 | 0.41 | 2564.4513 | 0.81 | 3604.5 | 1.21 | 4405.5 | 1.61 | 5081.7753 | 2.01 | 5678.0675 | 2.41 | 6217.432 | 2.81 | 6713.6034 | 3.21 | 7175.5474 | 3.61 | 7609.5 | 4.01 | 8020.0062 | 4.41 | 8410.5 | 4.81 | 8783.6507
0.02 | 566.3925 | 0.42 | 2595.5366 | 0.82 | 3626.6817 | 1.22 | 4423.6671 | 1.62 | 5097.5328 | 2.02 | 5692.1745 | 2.42 | 6230.3178 | 2.82 | 6725.5387 | 3.22 | 7186.7156 | 3.62 | 7620.0322 | 4.02 | 8030 | 4.42 | 8420.0303 | 4.82 | 8792.7766
0.03 | 693.6863 | 0.43 | 2626.2541 | 0.83 | 3648.7286 | 1.23 | 4441.7599 | 1.63 | 5113.2417 | 2.03 | 5706.2466 | 2.43 | 6243.1771 | 2.83 | 6737.4528 | 3.23 | 7197.8664 | 3.63 | 7630.5498 | 4.03 | 8039.9814 | 4.43 | 8429.5499 | 4.83 | 8801.893
0.04 | 801 | 0.44 | 2656.6165 | 0.84 | 3670.6431 | 1.24 | 4459.7793 | 1.64 | 5128.9025 | 2.04 | 5720.2842 | 2.44 | 6256.01 | 2.84 | 6749.346 | 3.24 | 7209 | 3.64 | 7641.053 | 4.04 | 8049.9504 | 4.44 | 8439.0587 | 4.84 | 8811
0.05 | 895.5452 | 0.45 | 2686.6357 | 0.85 | 3692.4276 | 1.25 | 4477.7261 | 1.65 | 5144.5156 | 2.05 | 5734.2873 | 2.45 | 6268.8166 | 2.85 | 6761.2182 | 3.25 | 7220.1164 | 3.65 | 7651.5418 | 4.05 | 8059.907 | 4.45 | 8448.5568 | 4.85 | 8820.0976
0.06 | 981.0206 | 0.46 | 2716.3232 | 0.86 | 3714.0842 | 1.26 | 4495.6014 | 1.66 | 5160.0815 | 2.06 | 5748.2564 | 2.46 | 6281.5971 | 2.86 | 6773.0696 | 3.26 | 7231.2158 | 3.66 | 7662.0162 | 4.06 | 8069.8514 | 4.46 | 8458.0442 | 4.86 | 8829.1858
0.07 | 1059.6234 | 0.47 | 2745.6897 | 0.87 | 3735.6153 | 1.27 | 4513.4058 | 1.67 | 5175.6006 | 2.07 | 5762.1916 | 2.47 | 6294.3516 | 2.87 | 6784.9003 | 3.27 | 7242.2981 | 3.67 | 7672.4762 | 4.07 | 8079.7835 | 4.47 | 8467.521 | 4.87 | 8838.2646
0.08 | 1132.7851 | 0.48 | 2774.7454 | 0.88 | 3757.023 | 1.28 | 4531.1403 | 1.68 | 5191.0733 | 2.08 | 5776.0931 | 2.48 | 6307.0803 | 2.88 | 6796.7104 | 3.28 | 7253.3635 | 3.68 | 7682.9221 | 4.08 | 8089.7035 | 4.48 | 8476.9872 | 4.88 | 8847.3342
0.09 | 1201.5 | 0.49 | 2803.5 | 0.89 | 3778.3094 | 1.29 | 4548.8056 | 1.69 | 5206.5 | 2.09 | 5789.9613 | 2.49 | 6319.7834 | 2.89 | 6808.5 | 3.29 | 7264.412 | 3.69 | 7693.3538 | 4.09 | 8099.6112 | 4.49 | 8486.4429 | 4.89 | 8856.3944
0.1 | 1266.4922 | 0.5 | 2831.9627 | 0.9 | 3799.4766 | 1.3 | 4566.4026 | 1.7 | 5221.8811 | 2.1 | 5803.7964 | 2.5 | 6332.461 | 2.9 | 6820.2692 | 3.3 | 7275.4438 | 3.7 | 7703.7713 | 4.1 | 8109.5069 | 4.5 | 8495.888 | 4.9 | 8865.4454
0.11 | 1328.3082 | 0.51 | 2860.1421 | 0.91 | 3820.5265 | 1.31 | 4583.932 | 1.71 | 5237.2171 | 2.11 | 5817.5985 | 2.51 | 6345.1133 | 2.91 | 6832.0182 | 3.31 | 7286.4589 | 3.71 | 7714.1748 | 4.11 | 8119.3905 | 4.51 | 8505.3226 | 4.91 | 8874.4872
0.12 | 1387.3727 | 0.52 | 2888.0466 | 0.92 | 3841.4611 | 1.32 | 4601.3947 | 1.72 | 5252.5083 | 2.12 | 5831.368 | 2.52 | 6357.7404 | 2.92 | 6843.747 | 3.32 | 7297.4573 | 3.72 | 7724.5643 | 4.12 | 8129.2621 | 4.52 | 8514.7468 | 4.92 | 8883.5197
0.13 | 1444.0233 | 0.53 | 2915.684 | 0.93 | 3862.2821 | 1.33 | 4618.7913 | 1.73 | 5267.755 | 2.13 | 5845.1051 | 2.53 | 6370.3425 | 2.93 | 6855.4557 | 3.33 | 7308.4392 | 3.73 | 7734.9398 | 4.13 | 8139.1218 | 4.53 | 8524.1606 | 4.93 | 8892.5431
0.14 | 1498.5338 | 0.54 | 2943.0619 | 0.94 | 3882.9916 | 1.34 | 4636.1227 | 1.74 | 5282.9578 | 2.14 | 5858.8099 | 2.54 | 6382.9197 | 2.94 | 6867.1445 | 3.34 | 7319.4046 | 3.74 | 7745.3014 | 4.14 | 8148.9695 | 4.54 | 8533.5639 | 4.94 | 8901.5574
0.15 | 1551.1298 | 0.55 | 2970.1875 | 0.95 | 3903.5911 | 1.35 | 4653.3895 | 1.75 | 5298.117 | 2.15 | 5872.4828 | 2.55 | 6395.4721 | 2.95 | 6878.8134 | 3.35 | 7330.3536 | 3.75 | 7755.6492 | 4.15 | 8158.8053 | 4.55 | 8542.957 | 4.95 | 8910.5625
0.16 | 1602 | 0.56 | 2997.0676 | 0.96 | 3924.0826 | 1.36 | 4670.5925 | 1.76 | 5313.2329 | 2.16 | 5886.1239 | 2.56 | 6408 | 2.96 | 6890.4625 | 3.36 | 7341.2863 | 3.76 | 7765.9831 | 4.16 | 8168.6293 | 4.56 | 8552.3397 | 4.96 | 8919.5585
0.17 | 1651.3038 | 0.57 | 3023.7087 | 0.97 | 3944.4675 | 1.37 | 4687.7323 | 1.77 | 5328.3059 | 2.17 | 5899.7334 | 2.57 | 6420.5034 | 2.97 | 6902.092 | 3.37 | 7352.2027 | 3.77 | 7776.3034 | 4.17 | 8178.4414 | 4.57 | 8561.7121 | 4.97 | 8928.5455
0.18 | 1699.1776 | 0.58 | 3050.1171 | 0.98 | 3964.7477 | 1.38 | 4704.8097 | 1.78 | 5343.3365 | 2.18 | 5913.3116 | 2.58 | 6432.9826 | 2.98 | 6913.7019 | 3.38 | 7363.1029 | 3.78 | 7786.6099 | 4.18 | 8188.2418 | 4.58 | 8571.0743 | 4.98 | 8937.5234
0.19 | 1745.739 | 0.59 | 3076.2989 | 0.99 | 3984.9247 | 1.39 | 4721.8254 | 1.79 | 5358.3248 | 2.19 | 5926.8588 | 2.59 | 6445.4375 | 2.99 | 6925.2924 | 3.39 | 7373.987 | 3.79 | 7796.9029 | 4.19 | 8198.0305 | 4.59 | 8580.4263 | 4.99 | 8946.4923
0.2 | 1791.0904 | 0.6 | 3102.2597 | 1 | 4005 | 1.4 | 4738.7799 | 1.8 | 5373.2713 | 2.2 | 5940.375 | 2.6 | 6457.8685 | 3 | 6936.8635 | 3.4 | 7384.8551 | 3.8 | 7807.1823 | 4.2 | 8207.8076 | 4.6 | 8589.768 | 5 | 8955.4522
0.21 | 1835.3216 | 0.61 | 3128.005 | 1.01 | 4024.9752 | 1.41 | 4755.674 | 1.81 | 5388.1764 | 2.21 | 5953.8605 | 2.61 | 6470.2755 | 3.01 | 6948.4153 | 3.41 | 7395.7072 | 3.81 | 7817.4481 | 4.21 | 8217.573 | 4.61 | 8599.0997 | 5.01 | 8964.4032
0.22 | 1878.5115 | 0.62 | 3153.5402 | 1.02 | 4044.8517 | 1.42 | 4772.5083 | 1.82 | 5403.0404 | 2.22 | 5967.3156 | 2.62 | 6482.6588 | 3.02 | 6959.948 | 3.42 | 7406.5434 | 3.82 | 7827.7005 | 4.22 | 8227.3268 | 4.62 | 8608.4212 | 5.02 | 8973.3453
0.23 | 1920.7305 | 0.63 | 3178.8702 | 1.03 | 4064.6311 | 1.43 | 4789.2834 | 1.83 | 5417.8636 | 2.23 | 5980.7404 | 2.63 | 6495.0185 | 3.03 | 6971.4615 | 3.43 | 7417.3638 | 3.83 | 7837.9395 | 4.23 | 8237.069 | 4.63 | 8617.7326 | 5.03 | 8982.2784
0.24 | 1962.0413 | 0.64 | 3204 | 1.04 | 4084.3146 | 1.44 | 4806 | 1.84 | 5432.6463 | 2.24 | 5994.1351 | 2.64 | 6507.3548 | 3.04 | 6982.9561 | 3.44 | 7428.1684 | 3.84 | 7848.1651 | 4.24 | 8246.7997 | 4.64 | 8627.034 | 5.04 | 8991.2027
0.25 | 2002.5 | 0.65 | 3228.9342 | 1.05 | 4103.9038 | 1.45 | 4822.6586 | 1.85 | 5447.3889 | 2.25 | 6007.5 | 2.65 | 6519.6676 | 3.05 | 6994.4318 | 3.45 | 7438.9573 | 3.85 | 7858.3775 | 4.25 | 8256.519 | 4.65 | 8636.3254 | 5.05 | 9000.1181
0.26 | 2042.1573 | 0.66 | 3253.6774 | 1.06 | 4123.3999 | 1.46 | 4839.2599 | 1.86 | 5462.0918 | 2.26 | 6020.8352 | 2.66 | 6531.9573 | 3.06 | 7005.8887 | 3.46 | 7449.7306 | 3.86 | 7868.5765 | 4.26 | 8266.2269 | 4.66 | 8645.6068 | 5.06 | 9009.0247
0.27 | 2081.059 | 0.67 | 3278.2338 | 1.07 | 4142.8042 | 1.47 | 4855.8044 | 1.87 | 5476.7551 | 2.27 | 6034.1409 | 2.67 | 6544.2239 | 3.07 | 7017.3269 | 3.47 | 7460.4884 | 3.87 | 7878.7624 | 4.27 | 8275.9233 | 4.67 | 8654.8782 | 5.07 | 9017.9225
0.28 | 2119.2468 | 0.68 | 3302.6076 | 1.08 | 4162.1181 | 1.48 | 4872.2928 | 1.88 | 5491.3793 | 2.28 | 6047.4174 | 2.68 | 6556.4676 | 3.08 | 7028.7465 | 3.48 | 7471.2306 | 3.88 | 7888.9351 | 4.28 | 8285.6084 | 4.68 | 8664.1397 | 5.08 | 9026.8116
0.29 | 2156.7585 | 0.69 | 3326.8029 | 1.09 | 4181.3428 | 1.49 | 4888.7255 | 1.89 | 5505.9647 | 2.29 | 6060.6648 | 2.69 | 6568.6884 | 3.09 | 7040.1475 | 3.49 | 7481.9574 | 3.89 | 7899.0947 | 4.29 | 8295.2822 | 4.69 | 8673.3913 | 5.09 | 9035.6919
0.3 | 2193.6288 | 0.7 | 3350.8234 | 1.1 | 4200.4794 | 1.5 | 4905.1032 | 1.9 | 5520.5115 | 2.3 | 6073.8832 | 2.7 | 6580.8865 | 3.1 | 7051.5302 | 3.5 | 7492.6689 | 3.9 | 7909.2413 | 4.3 | 8304.9448 | 4.7 | 8682.6331 | 5.1 | 9044.5634
0.31 | 2229.8896 | 0.71 | 3374.673 | 1.11 | 4219.5293 | 1.51 | 4921.4264 | 1.91 | 5535.0201 | 2.31 | 6087.073 | 2.71 | 6593.0621 | 3.11 | 7062.8944 | 3.51 | 7503.3651 | 3.91 | 7919.3748 | 4.31 | 8314.5961 | 4.71 | 8691.865 | 5.11 | 9053.4263
0.32 | 2265.5701 | 0.72 | 3398.3552 | 1.12 | 4238.4936 | 1.52 | 4937.6956 | 1.92 | 5549.4908 | 2.32 | 6100.2343 | 2.72 | 6605.2152 | 3.12 | 7074.2405 | 3.52 | 7514.046 | 3.92 | 7929.4954 | 4.32 | 8324.2362 | 4.72 | 8701.0872 | 5.12 | 9062.2805
0.33 | 2300.6973 | 0.73 | 3421.8735 | 1.13 | 4257.3734 | 1.53 | 4953.9114 | 1.93 | 5563.9238 | 2.33 | 6113.3672 | 2.73 | 6617.346 | 3.13 | 7085.5683 | 3.53 | 7524.7118 | 3.93 | 7939.6032 | 4.33 | 8333.8651 | 4.73 | 8710.2995 | 5.13 | 9071.1261
0.34 | 2335.2962 | 0.74 | 3445.2313 | 1.14 | 4276.1698 | 1.54 | 4970.0743 | 1.94 | 5578.3195 | 2.34 | 6126.4719 | 2.74 | 6629.4546 | 3.14 | 7096.8781 | 3.54 | 7535.3625 | 3.94 | 7949.698 | 4.34 | 8343.483 | 4.74 | 8719.5022 | 5.14 | 9079.963
0.35 | 2369.39 | 0.75 | 3468.4317 | 1.15 | 4294.884 | 1.55 | 4986.1848 | 1.95 | 5592.6781 | 2.35 | 6139.5487 | 2.75 | 6641.5411 | 3.15 | 7108.1699 | 3.55 | 7545.9982 | 3.95 | 7959.7801 | 4.35 | 8353.0898 | 4.75 | 8728.6951 | 5.15 | 9088.7914
0.36 | 2403 | 0.76 | 3491.4781 | 1.16 | 4313.517 | 1.56 | 5002.2434 | 1.96 | 5607 | 2.36 | 6152.5977 | 2.76 | 6653.6057 | 3.16 | 7119.4437 | 3.56 | 7556.6189 | 3.96 | 7969.8494 | 4.36 | 8362.6855 | 4.76 | 8737.8784 | 5.16 | 9097.6112
0.37 | 2436.1464 | 0.77 | 3514.3732 | 1.17 | 4332.0699 | 1.57 | 5018.2506 | 1.97 | 5621.2854 | 2.37 | 6165.6191 | 2.77 | 6665.6484 | 3.17 | 7130.6998 | 3.57 | 7567.2247 | 3.97 | 7979.906 | 4.37 | 8372.2703 | 4.77 | 8747.052 | 5.17 | 9106.4224
0.38 | 2468.8478 | 0.78 | 3537.1202 | 1.18 | 4350.5436 | 1.58 | 5034.2069 | 1.98 | 5635.5345 | 2.38 | 6178.6131 | 2.78 | 6677.6695 | 3.18 | 7141.9381 | 3.58 | 7577.8156 | 3.98 | 7989.9499 | 4.38 | 8381.844 | 4.78 | 8756.216 | 5.18 | 9115.2251
0.39 | 2501.1217 | 0.79 | 3559.7219 | 1.19 | 4368.9392 | 1.59 | 5050.1128 | 1.99 | 5649.7478 | 2.39 | 6191.5797 | 2.79 | 6689.6689 | 3.19 | 7153.1587 | 3.59 | 7588.3918 | 3.99 | 7999.9812 | 4.39 | 8391.4069 | 4.79 | 8765.3705 | 5.19 | 9124.0194
0.4 | 2532.9844 | 0.8 | 3582.1809 | 1.2 | 4387.2577 | 1.6 | 5065.9688 | 2 | 5663.9253 | 2.4 | 6204.5193 | 2.8 | 6701.6468 | 3.2 | 7164.3618 | 3.6 | 7598.9532 | 4 | 8010 | 4.4 | 8400.9589 | 4.8 | 8774.5154 | 5.2 | 9132.8052

## System A - As Found
Location # | TP-1 |  |  | Location # | TP-2 |  |  | Location # | TP-3A |  |  | Location # | TP-3
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.6 | 3102.2597 | 422.7906 | 1 | 0.4 | 2532.9844 | 345.2071 | 1 | 0.88 | 3757.023 | 327.6959 | 1 | 0.43 | 2626.2541 | 357.9183
2 | 0.46 | 2716.3232 | 370.1933 | 2 | 0.34 | 2335.2962 | 318.2652 | 2 | 0.83 | 3648.7286 | 318.2502 | 2 | 0.45 | 2686.6357 | 366.1474
3 | 0.45 | 2686.6357 | 366.1474 | 3 | 0.35 | 2369.39 | 322.9117 | 3 | 0.89 | 3778.3094 | 329.5525 | 3 | 0.41 | 2564.4513 | 349.4955
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.50333 | 2841.3869 | 387.2376 | Average | 0.36333 | 2414.0994 | 329.0049 | Average | 0.86667 | 3728.4521 | 325.2039 | Average | 0.43 | 2626.2541 | 357.9183
Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 4 | 0.087222 |  |  | 5 | 0.13628
Location # | TP-4A |  |  | Location # | TP-4 |  |  | Location # | TP-5A |  |  | Location # | TP-5
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.85 | 3692.4276 | 322.0617 | 1 | 0.1 | 1266.4922 | 172.6035 | 1 | 0.77 | 3514.3732 | 306.5314 | 1 | 0.43 | 2626.2541 | 357.9183
2 | 0.876 | 3748.4746 | 326.9503 | 2 | 0.11 | 1328.3082 | 181.0281 | 2 | 0.77 | 3514.3732 | 306.5314 | 2 | 0.38 | 2468.8478 | 336.4662
3 | 0.86 | 3714.0842 | 323.9507 | 3 | 0.12 | 1387.3727 | 189.0777 | 3 | 0.63 | 3178.8702 | 277.2681 | 3 | 0.33 | 2300.6973 | 313.5499
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.862 | 3718.4004 | 324.3271 | Average | 0.11 | 1328.3082 | 181.0281 | Average | 0.72333 | 3406.2127 | 297.0974 | Average | 0.38 | 2468.8478 | 336.4662
Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 4 | 0.087222 |  |  | 5 | 0.13628 |  |  | 4 | 0.087222 |  |  | 5 | 0.13628
Location # | TP-6A |  |  | Location # | TP-6 |  |  | Location # | TP-7A |  |  | Location # | TP-7
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.6 | 3102.2597 | 270.586 | 1 | 0.25 | 2002.5 | 272.9102 | 1 | 0.81 | 3604.5 | 314.3925 | 1 | 0.41 | 2564.4513 | 349.4955
2 | 0.74 | 3445.2313 | 300.5007 | 2 | 0.56 | 2997.0676 | 408.4545 | 2 | 0.8 | 3582.1809 | 312.4458 | 2 | 0.4 | 2532.9844 | 345.2071
3 | 0.7 | 3350.8234 | 292.2663 | 3 | 0.52 | 2888.0466 | 393.5966 | 3 | 0.82 | 3626.6817 | 316.3272 | 3 | 0.31 | 2229.8896 | 303.8999
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.68 | 3302.6076 | 288.0608 | Average | 0.44333 | 2666.6604 | 363.4251 | Average | 0.81 | 3604.5 | 314.3925 | Average | 0.37333 | 2447.0954 | 333.5017
Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 4 | 0.087222 |  |  | 5 | 0.13628 |  |  | 4 | 0.087222 |  |  | 5 | 0.13628
Location # | TP-8A |  |  | Location # | TP-8 |  |  | Location # | TP-9A |  |  | Location # | TP-9
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.82 | 3626.6817 | 316.3272 | 1 | 0.45 | 2686.6357 | 366.1474 | 1 | 0.85 | 3692.4276 | 322.0617 | 1 | 0.4 | 2532.9844 | 345.2071
2 | 0.8 | 3582.1809 | 312.4458 | 2 | 0.43 | 2626.2541 | 357.9183 | 2 | 0.79 | 3559.7219 | 310.4869 | 2 | 0.4 | 2532.9844 | 345.2071
3 | 0.77 | 3514.3732 | 306.5314 | 3 | 0.5 | 2831.9627 | 385.9532 | 3 | 0.79 | 3559.7219 | 310.4869 | 3 | 0.39 | 2501.1217 | 340.8647
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.79667 | 3574.7102 | 311.7942 | Average | 0.46 | 2716.3232 | 370.1933 | Average | 0.81 | 3604.5 | 314.3925 | Average | 0.39667 | 2522.4082 | 343.7657
Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 4 | 0.087222 |  |  | 5 | 0.13628 |  |  | 4 | 0.087222 |  |  | 5 | 0.13628
Location # | TP-10A |  |  | Location # | TP-10 |  |  | Location # | TP-11A |  |  | Location # | TP-11
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.63 | 3178.8702 | 277.2681 | 1 | 0.48 | 2774.7454 | 378.1554 | 1 | 0.52 | 2888.0466 | 251.9018 | 1 | 0.27 | 2081.059 | 283.6166
2 | 0.75 | 3468.4317 | 302.5243 | 2 | 0.42 | 2595.5366 | 353.732 | 2 | 0.26 | 2042.1573 | 178.1215 | 2 | 0.24 | 1962.0413 | 267.3963
3 | 0.85 | 3692.4276 | 322.0617 | 3 | 0.42 | 2595.5366 | 353.732 | 3 | 0.23 | 1920.7305 | 167.5304 | 3 | 0.22 | 1878.5115 | 256.0124
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.74333 | 3452.9821 | 301.1768 | Average | 0.44 | 2656.6165 | 362.0562 | Average | 0.33667 | 2323.8205 | 202.6888 | Average | 0.24333 | 1975.6196 | 269.2468
Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 4 | 0.087222 |  |  | 5 | 0.13628 |  |  | 4 | 0.087222 |  |  | 5 | 0.13628
Location # | TP-12A |  |  | Location # | TP-12 |  |  | Location # | TP-13 |  |  | Location # | TP-14
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.39 | 2501.1217 | 218.1534 | 1 | 0.39 | 2501.1217 | 340.8647 | 1 | 0.23 | 1920.7305 | 261.7662 | 1 | 0.25 | 2002.5 | 272.9102
2 | 0.29 | 2156.7585 | 188.1173 | 2 | 0.29 | 2156.7585 | 293.9332 | 2 | 0.22 | 1878.5115 | 256.0124 | 2 | 0.24 | 1962.0413 | 267.3963
3 | 0.43 | 2626.2541 | 229.0677 | 3 | 0.43 | 2626.2541 | 357.9183 | 3 | 0.2 | 1791.0904 | 244.0983 | 3 | 0.26 | 2042.1573 | 278.3148
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.37 | 2436.1464 | 212.4861 | Average | 0.37 | 2436.1464 | 332.0095 | Average | 0.21667 | 1864.226 | 254.0655 | Average | 0.25 | 2002.5 | 272.9102
Duct Area: | 0.087222 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 4 | 0.087222 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628
Location # | TP-15 |  |  | Location # | TP-16 |  |  | Location # | TP-17 |  |  | Location # | TP-18
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.33 | 2300.6973 | 313.5499 | 1 | 0.24 | 1962.0413 | 267.3963 | 1 | 0.16 | 1602 | 218.3281 | 1 | 0.15 | 1551.1298 | 211.3953
2 | 0.25 | 2002.5 | 272.9102 | 2 | 0.22 | 1878.5115 | 256.0124 | 2 | 0.13 | 1444.0233 | 196.7983 | 2 | 0.18 | 1699.1776 | 231.5719
3 | 0.4 | 2532.9844 | 345.2071 | 3 | 0.24 | 1962.0413 | 267.3963 | 3 | 0.17 | 1651.3038 | 225.0475 | 3 | 0.18 | 1699.1776 | 231.5719
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.32667 | 2289.0482 | 311.9623 | Average | 0.23333 | 1934.5988 | 263.6563 | Average | 0.15333 | 1568.2699 | 213.7312 | Average | 0.17 | 1651.3038 | 225.0475
Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628
Location # | TP-19 |  |  | Location # | TP-20 |  |  | Location # | TP-21
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.33 | 2300.6973 | 313.5499 | 1 | 0.16 | 1602 | 218.3281 | 1 | 0.68 | 3302.6076 | 4608.9724
2 | 0.32 | 2265.5701 | 308.7626 | 2 | 0.15 | 1551.1298 | 211.3953 | 2 | 0.84 | 3670.6431 | 5122.5864
3 | 0.25 | 2002.5 | 272.9102 | 3 | 0.18 | 1699.1776 | 231.5719 | 3 | 0.87 | 3735.6153 | 5213.2587
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 | 0.86 | 3714.0842 | 5183.2108
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 | 0.85 | 3692.4276 | 5152.9878
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 | 0.86 | 3714.0842 | 5183.2108
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 | 0.87 | 3735.6153 | 5213.2587
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.3 | 2193.6288 | 298.9581 | Average | 0.16333 | 1618.6015 | 220.5907 | Average | 0.83286 | 3655.0033 | 5100.7602
Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 1.3956
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter
| 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 16 | 1.3956

## System A - As left
Location # | TP-1 |  |  | Location # | TP-2 |  |  | Location # | TP-3 |  |  | Location # | TP-4
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.31 | 2229.8896 | 303.8999 | 1 | 0.33 | 2300.6973 | 313.5499 | 1 | 0.34 | 2335.2962 | 318.2652 | 1 | 0.38 | 2468.8478 | 336.4662
2 | 0.32 | 2265.5701 | 308.7626 | 2 | 0.37 | 2436.1464 | 332.0095 | 2 | 0.35 | 2369.39 | 322.9117 | 2 | 0.4 | 2532.9844 | 345.2071
3 | 0.38 | 2468.8478 | 336.4662 | 3 | 0.31 | 2229.8896 | 303.8999 | 3 | 0.39 | 2501.1217 | 340.8647 | 3 | 0.35 | 2369.39 | 322.9117
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.33667 | 2323.8205 | 316.7012 | Average | 0.33667 | 2323.8205 | 316.7012 | Average | 0.36 | 2403 | 327.4922 | Average | 0.37667 | 2457.9957 | 334.9873
Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter | [7 empty] | Diameter
| 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628
Location # | TP-5 |  |  | Location # | TP-6 |  |  | Location # | TP-7 |  |  | Location # | TP-8
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.19 | 1745.739 | 237.9176 | 1 | 0.38 | 2468.8478 | 336.4662 | 1 | 0.23 | 1920.7305 | 261.7662 | 1 | 0.4 | 2532.9844 | 345.2071
2 | 0.26 | 2042.1573 | 278.3148 | 2 | 0.41 | 2564.4513 | 349.4955 | 2 | 0.51 | 2860.1421 | 389.7937 | 2 | 0.68 | 3302.6076 | 450.095
3 | 0.67 | 3278.2338 | 446.7732 | 3 | 0.36 | 2403 | 327.4922 | 3 | 0.52 | 2888.0466 | 393.5966 | 3 | 0.6 | 3102.2597 | 422.7906
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.37333 | 2447.0954 | 333.5017 | Average | 0.38333 | 2479.6524 | 337.9387 | Average | 0.42 | 2595.5366 | 353.732 | Average | 0.56 | 2997.0676 | 408.4545
Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628
Location # | TP-9 |  |  | Location # | TP-10 |  |  | Location # | TP-11 |  |  | Location # | TP-12
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.32 | 2265.5701 | 308.7626 | 1 | 0.42 | 2595.5366 | 353.732 | 1 | 0.37 | 2436.1464 | 332.0095 | 1 | 0.34 | 2335.2962 | 318.2652
2 | 0.42 | 2595.5366 | 353.732 | 2 | 0.23 | 1920.7305 | 261.7662 | 2 | 0.39 | 2501.1217 | 340.8647 | 2 | 0.31 | 2229.8896 | 303.8999
3 | 0.47 | 2745.6897 | 374.1956 | 3 | 0.36 | 2403 | 327.4922 | 3 | 0.27 | 2081.059 | 283.6166 | 3 | 0.28 | 2119.2468 | 288.821
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.40333 | 2543.5166 | 346.6425 | Average | 0.33667 | 2323.8205 | 316.7012 | Average | 0.34333 | 2346.7158 | 319.8215 | Average | 0.31 | 2229.8896 | 303.8999
Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628
Location # | TP-13 |  |  | Location # | TP-14 |  |  | Location # | TP-15 |  |  | Location # | TP-16
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.28 | 2119.2468 | 288.821 | 1 | 0.22 | 1878.5115 | 256.0124 | 1 | 0.23 | 1920.7305 | 261.7662 | 1 | 0.19 | 1745.739 | 237.9176
2 | 0.27 | 2081.059 | 283.6166 | 2 | 0.25 | 2002.5 | 272.9102 | 2 | 0.25 | 2002.5 | 272.9102 | 2 | 0.22 | 1878.5115 | 256.0124
3 | 0.2 | 1791.0904 | 244.0983 | 3 | 0.26 | 2042.1573 | 278.3148 | 3 | 0.19 | 1745.739 | 237.9176 | 3 | 0.25 | 2002.5 | 272.9102
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.25 | 2002.5 | 272.9102 | Average | 0.24333 | 1975.6196 | 269.2468 | Average | 0.22333 | 1892.6892 | 257.9446 | Average | 0.22 | 1878.5115 | 256.0124
Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628
Location # | TP-17 |  |  | Location # | TP-18 |  |  | Location # | TP-19 |  |  | Location # | TP-20
Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM | Test Point | VP | V | CFM
1 | 0.19 | 1745.739 | 237.9176 | 1 | 0.21 | 1835.3216 | 250.1263 | 1 | 0.17 | 1651.3038 | 225.0475 | 1 | 0.26 | 2042.1573 | 278.3148
2 | 0.2 | 1791.0904 | 244.0983 | 2 | 0.19 | 1745.739 | 237.9176 | 2 | 0.23 | 1920.7305 | 261.7662 | 2 | 0.22 | 1878.5115 | 256.0124
3 | 0.23 | 1920.7305 | 261.7662 | 3 | 0.2 | 1791.0904 | 244.0983 | 3 | 0.18 | 1699.1776 | 231.5719 | 3 | 0.25 | 2002.5 | 272.9102
4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0 | 4 |  | 0 | 0
5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0 | 5 |  | 0 | 0
6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0 | 6 |  | 0 | 0
7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0 | 7 |  | 0 | 0
8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0 | 8 |  | 0 | 0
9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0 | 9 |  | 0 | 0
10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0 | 10 |  | 0 | 0
11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0 | 11 |  | 0 | 0
12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0 | 12 |  | 0 | 0
13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0 | 13 |  | 0 | 0
14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0 | 14 |  | 0 | 0
15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0 | 15 |  | 0 | 0
Average | 0.20667 | 1820.6973 | 248.1332 | Average | 0.2 | 1791.0904 | 244.0983 | Average | 0.19333 | 1760.9859 | 239.9955 | Average | 0.24333 | 1975.6196 | 269.2468
Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628 |  |  | Duct Area: | 0.13628
Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF |  | Length | Width | Area SF
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Diameter |  |  |  | Diameter |  |  |  | Diameter |  |  |  | Diameter
| 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628 |  |  | 5 | 0.13628
Location # | TP-21
Test Point | VP | V | CFM
1 | 0.83 | 3648.7286 | 5092.0035
2 | 0.87 | 3735.6153 | 5213.2587
3 | 0.82 | 3626.6817 | 5061.2359
4 | 0.73 | 3421.8735 | 4775.4146
5 | 0.71 | 3374.673 | 4709.5436
6 | 0.76 | 3491.4781 | 4872.5516
7 | 0.78 | 3537.1202 | 4936.2478
8 |  | 0 | 0 | Static Pressure = 3.56 inwc
9 |  | 0 | 0
10 |  | 0 | 0
11 |  | 0 | 0
12 |  | 0 | 0
13 |  | 0 | 0
14 |  | 0 | 0
15 |  | 0 | 0
Average | 0.78571 | 3550.0531 | 4954.2963
Duct Area: | 1.3956
Length | Width | Area SF
0
Diameter
| 16 | 1.3956