System Checkout

Spartanburg Community College

Gaffney, SC

When I arrived on site fan would not start from ethers set of control switches.  When started from the VFD Local push button the fan can up to 40 HZ. In trying different VFD setting, I found that if I pushed the Auto push button on the VFD than both sets of start/stop buttons operated as designed. I checked and set the pulse timer board and it operated as it should.

I tried turning off the main power and then turning it back on.  When the  VFD came back on it was still in the Auto Mode and both sets of start/stop buttons still operated.

The speed of the fan could be controlled from the VFD panel on the front of the Main Control Panel.

I check the air flow and got the following reading:

At 60 HZ the main trunk I got 18,500 CFM. The required flow is 12,500CFM

At 40 HZ the main trunk I got 12,513 CFM. The VFD is set to start at 40 HZ.

In looking at the bid spec I am not sure if we have met the spec.  To be sure I will need to study the diagram for the control panel and the spec sheets for the pulse time (I have them in my possession). I would like to get the control panel diagram in AutoCAD, if possible, so that I can add the changes that Spartanburg CC has made so that I can see just how all the interfaces operate.

Report respectfully submitted,

Bill Boisvert

Bill Boisvert, Project Specialist

Avani Environmental Intl., Inc.®

An Absolent Group Company

95 Cypress Drive, Youngsville, North Carolina 27596

Cell: 919-971-3910 - Office: 919-488-5195

E-mail: bboisvert@avanienvironmental.com