Date: 	6/5/08	  	     Project#:  		           IAQ Crew:  Bill B., James W.

Customer:	Systrand Presta				Installation:  X

70 Waltz Creek				Service:

Danville, IL 61834				Warranty:

Repair:

# Scope Of Project

- Connected one grinder to Line 1/A1

  - Installed 12/8/12 branch

  - Ran duct from grinder to installed branch

    - Line included butterfly damper and fire damper

  - Cleaned area

  - Inspected ODR-3000 – found gauge line to HEPA gauge inside unit disconnected.  To replaced line filter needs to be removed, gauge line blown out and replaced on fitting number one inside unit.  Remove gauge access panel on back of door and blow out gauge line from gauge to fitting number one. Replace filter.

- Connected one grinder to Line 1/A2

  - Installed 12/8/12 branch

  - Ran duct from grinder to installed branch

    - Line included butterfly damper and fire damper

  - Cleaned area

  - Inspected ODR-3000 – found gauge line to HEPA gauge inside unit disconnected.  To replaced line filter needs to be removed, gauge line blown out and replaced on fitting number one inside unit.  Remove gauge access panel on back of door and blow out gauge line from gauge to fitting number one. Replace filter.

- Installed hood and ran 8” duct to Torit DryFlow units on two Oberlin machines.

- Installed control packages in four ODR-3000’s.

- Straightened ductwork on new ODR-3000 system.

Ryan,

Please review and sign page two.  Feel free to make any comments that you feel are necessary.  After you sign please fax page two back to our office (919-562-7182).

Thanks,

Bill Boisvert

CUSTOMER REMARKS:

CUSTOMER SIGNATURE:						DATE:

TITLE OR DEPARTMENT: