## Sheet1
3000 | fpm
cfm | Size | Selected | Sq Inches | Velocity | VP | SP/100ft | 34 | Velocity | VP | SP/100ft
800 | 6.9923 | 6 | 28.2743 | 4074.37 | 1.0349 | 4.5
1600 | 9.8886 | 10 | 78.5397 | 2933.5464 | 0.53651 | 1.25
2400 | 12.111 | 12 | 113.0972 | 3055.7775 | 0.58215 | 1.1
3200 | 13.9846 | 14 | 153.9379 | 2993.4147 | 0.55864 | 1
4000 | 15.6353 | 16 | 201.0618 | 2864.7914 | 0.51166 | 0.69
4800 | 17.1276 | 16 | 201.0618 | 3437.7497 | 0.73679 | 0.98
5600 | 18.4999 | 16 | 201.0618 | 4010.708 | 1.0029 | 1.3
6400 | 19.7772 | 18 | 254.4688 | 3621.6622 | 0.81773 | 0.95
7200 | 20.9769 | 20 | 314.159 | 3300.2397 | 0.67903 | 0.68
8000 | 22.1116 | 22 | 380.1324 | 3030.5231 | 0.57257 | 0.52
8800 | 23.1909 | 22 | 380.1324 | 3333.5754 | 0.69281 | 0.64
9600 | 24.2221 | 24 | 452.389 | 3055.7775 | 0.58215 | 0.47
10400 | 25.2111 | 24 | 452.389 | 3310.4256 | 0.68322 | 0.55
11200 | 26.1628 | 24 | 452.389 | 3565.0737 | 0.79238 | 0.65
12000 | 27.0811 | 24 | 452.389 | 3819.7219 | 0.90962 | 0.72
12800 | 27.9693 | 28 | 615.7516 | 2993.4147 | 0.55864
13600 | 28.83 | 28 | 615.7516 | 3180.5031 | 0.63065
14400 | 29.6659 | 30 | 706.8578 | 2933.5464 | 0.53651
15200 | 30.4788 | 30 | 706.8578 | 3096.5212 | 0.59778
16000 | 31.2706 | 32 | 804.247 | 2864.7914 | 0.51166
16800 | 32.0428 | 32 | 804.247 | 3008.031 | 0.5641
17600 | 32.7969 | 34 | 907.9195 | 2791.4369 | 0.48579
18400 | 33.534 | 34 | 907.9195 | 2918.3204 | 0.53096
19200 | 34.2552 | 34 | 907.9195 | 3045.2039 | 0.57813
20000 | 34.9616 | 36 | 1017.8752 | 2829.4236 | 0.4991
20800 | 35.6539 | 36 | 1017.8752 | 2942.6005 | 0.53983
21600 | 36.3331 | 36 | 1017.8752 | 3055.7775 | 0.58215
22400 | 36.9998 | 38 | 1134.114 | 2844.1585 | 0.50432
23200 | 37.6548 | 38 | 1134.114 | 2945.7356 | 0.54098 |  | 32 | 3176.4706 | 0.62905 | 0.36
24000 | 38.2985 | 38 | 1134.114 | 3047.3127 | 0.57893 |  | 32 | 3282.3529 | 0.67168 | 0.38
24800 | 38.9316 | 40 | 1256.636 | 2841.8731 | 0.50351 |  | 34 | 3188.9273 | 0.63399 | 0.32
25600 | 39.5545 | 40 | 1256.636 | 2933.5464 | 0.53651 |  | 34 | 3288.5813 | 0.67424 | 0.33
26400 | 40.1678 | 40 | 1256.636 | 3025.2197 | 0.57057 |  | 34 | 3388.2353 | 0.71572 | 0.35
27200 | 40.7718 | 40 | 1256.636 | 3116.893 | 0.60567 |  | 38.5222
28000 | 41.3671 | 42 | 1385.4412 | 2910.2643 | 0.52803 |  | 39.6552
28800 | 41.9539 | 42 | 1385.4412 | 2993.4147 | 0.55864 |  | 40.7882
v | vp | sp
3000 | 0.5611

## Static Components
South Leg 12,000 cfm
Size |  | Description | cfm | SP/100 ft | Length | SP | Velocity
6 |  | Avani Arm | 700 | 4 | 100 | 4 | 3565.0737
6 |  | Drop | 700 | 3.4 | 6 | 0.204 | 3565.0737
6 |  | Main | 700 | 3.4 | 6 | 0.204 | 3565.0737
10 |  | Main | 1400 | 1 | 6 | 0.06 | 2566.8531
12 |  | Main | 2100 | 0.85 | 6 | 0.051 | 2673.8053
14 |  | Main | 2800 | 0.7 | 6 | 0.042 | 2619.2378
14 |  | Main | 3500 | 1.05 | 6 | 0.063 | 3274.0473
16 |  | Main | 4200 | 0.75 | 6 | 0.045 | 3008.031
16 |  | 90 & Main | 4900 | 1 | 35 | 0.35 | 3509.3695
18 |  | Main | 5600 | 0.72 | 6 | 0.0432 | 3168.9544
18 |  | Main | 6300 | 0.9 | 6 | 0.054 | 3565.0737
20 |  | Main | 7000 | 0.65 | 6 | 0.039 | 3208.5664
20 |  | Main | 7700 | 0.8 | 6 | 0.048 | 3529.423
22 |  | Main | 8400 | 0.56 | 6 | 0.0336 | 3182.0493
22 |  | Main | 9100 | 0.67 | 6 | 0.0402 | 3447.2201
24 |  | Main | 9800 | 0.5 | 6 | 0.03 | 3119.4395
24 |  | Main | 10500 | 0.58 | 6 | 0.0348 | 3342.2566
5.3418
North Leg 11,200 cfm
Size |  | Description | cfm | SP/100 ft | Length | SP | Velocity
6 |  | Avani Arm | 700 | 4 | 100 | 4 | 3565.0737
6 |  | Drop | 700 | 3.4 | 6 | 0.204 | 3565.0737
6 |  | Main | 700 | 3.4 | 6 | 0.204 | 3565.0737
10 |  | Main | 1400 | 1 | 6 | 0.06 | 2566.8531
12 |  | Main | 2100 | 0.85 | 6 | 0.051 | 2673.8053
14 |  | Main | 3500 | 1.05 | 3 | 0.0315 | 3274.0473
16 |  | Main | 4200 | 0.75 | 6 | 0.045 | 3008.031
16 |  | Main | 4900 | 1 | 6 | 0.06 | 3509.3695
18 |  | Main | 5600 | 0.72 | 6 | 0.0432 | 3168.9544
18 |  | Main | 6300 | 0.9 | 6 | 0.054 | 3565.0737
20 |  | 90 & Main | 7000 | 0.65 | 23 | 0.1495 | 3208.5664
20 |  | Main | 7700 | 0.8 | 14 | 0.112 | 3529.423
24 |  | Main | 9800 | 0.5 | 42 | 0.21 | 3119.4395
5.2242
Twin Branch, North Leg 1,600 cfm
Size |  | Description | cfm | SP/100 ft | Length | SP | Velocity
6 |  | Avani Arm | 700 | 4 | 100 | 4 | 3565.0737
6 |  | Drop | 700 | 3.4 | 6 | 0.204 | 3565.0737
10 |  | Main | 1400 | 1 | 15 | 0.15 | 2566.8531
14 |  | Main | 3500 | 1.05 | 3 | 0.0315 | 3274.0473
16 |  | Main | 4200 | 0.75 | 6 | 0.045 | 3008.031
16 |  | Main | 4900 | 1 | 6 | 0.06 | 3509.3695
18 |  | Main | 5600 | 0.72 | 6 | 0.0432 | 3168.9544
18 |  | Main | 6300 | 0.9 | 6 | 0.054 | 3565.0737
20 |  | 90 & Main | 7000 | 0.65 | 23 | 0.1495 | 3208.5664
20 |  | Main | 7700 | 0.8 | 14 | 0.112 | 3529.423
24 |  | Main | 9800 | 0.5 | 42 | 0.21 | 3119.4395
5.0592
Tee to Filter
W | D | Description | cfm | SP/100 ft | Length | SP | Velocity
34 | 28 | Main | 20300 | 0.34 | 4 | 0.0136 | 3070.5882
34 | 28 | Main | 21000 | 0.36 | 6 | 0.0216 | 3176.4706
34 | 30 | Main | 21700 | 0.34 | 6 | 0.0204 | 3063.5294
34 | 30 | Main | 22400 | 0.36 | 6 | 0.0216 | 3162.3529
34 | 32 | Main | 23100 | 0.35 | 18 | 0.063 | 3057.3529
20 |  | Tap to Filter | 18400 | 4 | 6 | 0.24 | 8433.9459
0.3802
Filter to Fan
36 | 14 | Drop | 18400 | 1.65 | 10 | 0.165 | 5257.1429
34 |  | Connection | 18400 | 0.28 | 10 | 0.028 | 2918.3204
0.193

## Static Summary
Summary | SP Loss | Selected
South Leg 12,000 cfm | 5.3418 | 5.3418
North Leg 11,200 cfm | 5.2242
Twin Branch, North Leg 1,600 cfm | 5.0592
Tee to Filter | 0.3802 | 0.3802
Filter | 6 | 6
Filter to Fan | 0.193 | 0.193
Sound Attenuator | 0.07 | 0.07
Discharge Air Duct | 0.25 | 0.25
Total SP |  | 12.235
The ACGIH Manual defines Capture Velocity as the minimum hood-induced air velocity necessary to capture and convey a contaminant. It offers the following table:
Arm CFM | 700
|  |  | Condition of Dispersion Containment | Example | Capture Velocity, fpm
|  |  | Released with practically no velocity into quiet air. | Evaporation tanks,degreasing | 50-100
|  |  | Released at low velocity into moderately still air. | Spray booths, container filling, welding, plating, pickling | 100-200
|  |  | Active generation into zone of rapid air motion. | Spray painting in shallow booth, barrel filling, conveyor loading | 200-500
|  |  | Released at high initial velocity into zone of very rapid air motion. | Grinding, abrasive blasting,tumbling. | 500-2000
The formula used for converting this capture velocity to required cfm is:
Q = V(5X2 + A) where.
Q= Required Exhaust Air Flow, cfm.
X= Distance From Hood Face To Point Of Contaminant Release, Feet.
A= Hood Face Area, Sq. Ft.
V= Capture Velocity, fpm, T Distance X.
Using this formula for various hose sizes, we come up with the following cfm requirements for cone shaped hoods. (Assuming a face velocity of 1500 fpm and a distance of 9-12 inches from the source.
• 4" Hose-350-425 cfm
• 5" Hose-475-550 cfm
• 6" Hose-625-675 cfm
• 8" Hose-800-950 cfm
• 10" Hose-1100-1250 cfm
NOTE: These are suggested airflows for welding fumes only. Applications such as dust or grinding collection require higher airflow and capture velocities.